## ⚠️ Disclaimer
⚡ HEN Real-Time Congestion Playbook
Hunt Energy Network ¦ For Internal NOC Use Only
IMPORTANT — Please read before using this tool
📋 Purpose
This playbook is a reference tool to help operators quickly assess congestion as it happens in real time. Use it to build situational awareness around constraints you're seeing on screen — not as a hard trigger or automated signal.
⚠️ Data Limitations
The shadow pricing, shift factors, and MCC estimates here are derived from a specific historical study period (Apr 2025 – May 2026). Values shown are approximations based on the best information available at the time of analysis. Nodes, shift factors, and priority designations should be treated as starting points — not hard numbers.
🔄 ERCOT Topology Changes Constantly
Transmission outages, new generation interconnections, seasonal load shifts, and topology changes mean the grid you're operating today may respond differently than the grid used in this analysis. A constraint that behaved predictably in the past may not behave the same way every night. ALWAYS reference current outage conditions before acting. TOPOLOGY IS CONSTANTLY CHANGING.
📝 Keep the Notes Column Current
This tool is only as good as the information we put into it. If you observe new patterns, updated line behavior, or anything that doesn't match what you're seeing — add a note. The Operator Notes column is the most valuable part of this sheet over time.
✅ How to Use
1. See congestion on a line → find it in the Line Lookup tab 2. Check Priority: 🟢 Active ¦ 🟡 Watch ¦ ⚫ Low Priority 3. Review Peak HE, Driver, and Primary Node & SF 4. Jump to seasonal tab (Summer/Fall/Winter/Spring) for that season's top lines 5. Use the MCC Calculator tab to compute your site's real-time MCC from a shadow price 6. Add observations to Operator Notes for the next shift
Hunt Energy Network ¦ RT Congestion Playbook ¦ For internal operator use only

## 📋 Line Lookup
HEN REAL-TIME CONGESTION PLAYBOOK — LINE LOOKUP
🟢 Active = Detailed analysis ¦ 🟡 Watch = Observed, limited data ¦ ⚫ Low Priority = Outage-only or insufficient shift factor ¦ Updated: May 2026
Line / Constraint | Priority | Season | Peak HE (Active Hrs) | Gen Level Trigger (What Drives It) | Primary Node | Shift Factor | MCC @ $500 SP | MCC @ $1,000 SP | MCC @ $2,000 SP | Other Active Nodes (SF) | Hold Strategy / Discharge Timing | Operator Notes
🟢 ACTIVE — Priority Lines (Detailed Analysis Completed)
TWINBU-HARGROVE 138KV | 🟢 Active | Summer and Winter | HE5, HE6, HE4 | West wind sub 5GW is when we see it strongest. Since the start of RTC + B this number has been closer to 3GW. | Russek (31.7%) | 31.66% | 158.325 | 316.65 | 633.3 | Hamilton (+6.8%) Fort Duncan (+4.4%) | Willing to sit on high pricing HE20-24. | Watch to see if there is a hard cut off at HE4. Switches over to LAKENASW-SAMATHIS
FORTMA-YELWJCKT 138KV | 🟢 Active | Structural congestion | HE20-23 | Mostly seen overnight. Correlated when west dips below coastal wind generation. West wind gen generally has to be below 3GW | Junction (50.0%) | 50% | 250 | 500 | 1000 | Russek (+3.2%)
TREADWEL-YELWJCKT 138KV | 🟢 Active | Mostly summer | HE17, HE18, HE19 | The primary driver for this congestion is high far west west wind + far west solar generation trying to push power up to the north DURING THE SOLAR WINDOW | Junction (46.8%) | 46.76% | 233.775 | 467.55 | 935.1 | — |  | MW overload is around 200MW. Once we get close to this # line starts to bind. There's typically a lot of line outages in the region when we see this congestion pop up, so once you see it pop up, look into the line outages that stack up
WESTEX | 🟢 Active | All | HE20, HE19, HE12 | See flare up in days of high renewable generation. Our renewable generation number is 40GW for wind and solar, during days of load below 75GW. During days were load can reach 85-90GW we need to see 46GW+ of wind and solar. Seen in all hours of the day but most common during solar ramps. Shows up overnight when west Gen reaches above 15GW with a relatively low load. | Diboll (19.4%) | 19.4% | 96.98 | 193.96 | 387.92 | Judkins (-71.8%) Saddleback (-71.6%) Russek (-66.0%) Olney (-55.8%) |  | During the peak months, I think we need 45+GW of renewables online for this congestion to pop up. Especially when load reached 85GW+.
LNGSW-PRLSW 345KV | 🟢 Active | All | HE1, HE2, HE24 | This congestion is seen mostly overnight. Main driver on this line is when we see west wind gen reach above 10GW but haven't seen exposure since July 2026 | Judkins (21.3%) | 21.33% | 106.645 | 213.29 | 426.58 | Saddleback (+20.4%) Russek (+7.0%)
E_PASP | 🟢 Active | All | HE20, HE19, HE18 | This congestion is seem mostly overnight. Main driver on this line is when we see west wind gen reach above 10GW. | Junction (4.0%) | 4% | 20 | 40 | 80 | Val Verde (-19.6%) Holcomb (-13.8%) Catarina (-8.6%)
PALOUSE-WOLFCAMP 138KV | 🟢 Active | All but strong in summer | HE16-18 strongest | Strongest pricing seen in the summer (hot). When RT West load gets up to 9GW we will see this, especially when solar is ramping offline. It's driven by strong Far West solar and strong west wind. The combination of (Far west solar + West Wind) being above 10GW is a good indicator that we will see this congestion from 5pm-7pmish. | Russek (30.6%) | 30.57% | 152.845 | 305.69 | 611.38 | — |  | When far west solar gen is ramping offline and South wind gen is ramping up, its common to see this congestion. Also need a decently high load from the west.
PILONCIL-NLARSW 138KV | 🟡 Watch | All | All hours, track wind | see this with really low coastal and south winds. Like sub 1GW for each. In the middle of the day, we can see this when coastal and south wind go down to 500MW in both regions (both have less than 500MW of gen) | Holcomb (23.8%) | 23.81% | 119.035 | 238.07 | 476.14 | Catarina (-26.5%) Fort Duncan (-13.0%) Hamilton (-9.4%) Val Verde (+7.6%) | really just important to track the wind. If South gen stays below 500MW and coastal is also below 500MW during middle of day with low west wind, could see this really flare up all day
NLARSW-PILONCIL 138KV | 🟢 Active | All | HE24, HE1, HE2 | This is a newer congestion… started in Nov 2025. see this congestion with coastal and south wind gen at 2.5GW+ with west wind dropping out or even below 10GW. Look to PILONCIL-NLARSW for negative congestion | Catarina (26.0%) | 26% | 130 | 260 | 520 | Fort Duncan (+12.0%) Holcomb (-9.0%) Hamilton (+8.6%) Val Verde (-6.0%)
MGSES-CATSW 345KV | 🟢 Active | All | HE23, HE19, HE20 | Newer congestion (start Nov 2025). Mostly see this congestion with cooler weather in the west creating higher load levels (9gw+) and wind sub 8GW. West wind is the major driver of this congestion. Common to see with west wind sub 3GW. | Judkins (30.0%) | 30% | 150 | 300 | 600 | Saddleback (+27.0%) Russek (+10.0%) Cisco (-8.0%) Olney (-7.0%)
CRDSW-OLNEY 69KV | 🟢 Active | spring and summer | HE15-18 | See this on hot days where North load reaches up to 22GW+ of demand with high amounts of renewable online (use WESTEX flairing up as basis). Want 42+GW of solar + wind generation. 26MW flow rating, this limits the amount of MW we can put on this line | Olney (78.7%) | 78.68% | 393.41 | 786.82 | 1573.64 | — | Marginal offer line | 6630_A_LN outage impacts this line (per Enverus). Strong solar production, 90+ DFW Temps and good west wind production cause congestion here. Deplete before HE20
STP-WAP 345KV | 🟢 Active | Summer | HE17, HE16, HE13 | Def has to do with houston load during the summer heat. When houston load reaches above 18GW+ we will see this flare up. Need STP nuke units online also… if one of them is offline, this weakens congestion. | Mainland (9.6%) | 9.57% | 47.85 | 95.7 | 191.4 | Val Verde (-11.3%) Holcomb (-9.5%) Catarina (-8.5%) Fort Duncan (-7.0%)
ESCONDID-GANSO 138KV | 🟢 Active | all | HE8, HE9, HE1 | HE 10 saw the most shadow pricing but morning all around get best pricing. We see this congestion with low wind generation online, especially the west goin sub 3GW. Mostly completely correlated with west wind. | Hamilton (40.4%) Fort Duncan (-26%) | 40.35% | 201.75 | 403.5 | 807 | Fort Duncan (-26.1%) Catarina (-9.4%) Russek (+5.0%) Holcomb (-4.4%)
LNGSW-CONSW 345KV | 🟢 Active | Summer | HE1, HE2, HE24 | Pretty well associated with high west wind gen. Prob 10GW+. Never really get shadow pricing above $400 here but we still have 20%sf at west sites. Also couples well with West RT load being over 9GW overnight | Judkins (21.3%) | 21.3% | 106.5 | 213 | 426 | Saddleback (+20.0%) Russek (+8.0%)
YELWJCKT-FORTMA 138KV | 🟢 Active | mostly spring/summer | HE7, HE6, HE5 | Very high west winds. See it the most at 13GW+ of west wind gen in offpeak hours and 10+GW of west wind gen in on-peak hours | Junction (-50%) |  |  |  |  | Junction (-50.0%) |  | Driven by West wind with demand in the east.
Legend: | 🟢 Active = detailed MCC analysis completed |  |  |  | — |  |  |  |  | —
🟡 WATCH — Lines to Monitor (Limited Data)
ASHERTON-CATARINA 138KV | 🟡 Watch | Summer | HE13, HE12, HE14 | All conesiton seen in solar window. Driven by super low coastal and south wind gen during the solar window. Maybe look into this more, doesn't seem load driven | Catarina (77.0%) | 76.98% | 384.91 | 769.82 | 1539.64 | Holcomb (+17.2%) Fort Duncan (-11.6%) Hamilton (-9.0%) |  | If this shows up during the down ramp, it's typically caused by a dying west wind.
MRVLY-ESTLD 69KV | 🟡 Watch | Not seasonal | HE20, HE19, HE21 | Also seems to be when we see north load reach above 15GW. Especially if it's the load leader by a big chunk on the grid. Look at 01/11 and 01/12 | Cisco (17.3%) | 17.35% | 86.74 | 173.48 | 346.96 | —
LPLMK-LPLNE 115KV | 🟡 Watch | all | HE21, HE22, HE20 | Don't have very strong shift factors out here in the west but active pretty often when west wind levels go below 5GW but it's actually strong panhandle winds that is the cause. | Judkins (1.6%) | 1.594% | 7.97 | 15.94 | 31.88 | — |  | Strong wind generation from panhandle during day time
HONDOCK-DEVINESW 69KV | 🟡 Watch | Post RTC | HE16, HE18, HE17 | Newer constraint that showed up in January. Was strongest in march and april. Skip this one too weak of shift factor. The drivers are strong west wind/solar and strong load in San Antonio. | — |  |  |  |  | Fort Duncan (-6.4%) Hamilton (-6.0%) Catarina (-5.0%)
I_FW_N | 🟡 Watch | fall | HE5, HE6, HE4 | Never really see enough shadow pricing to create strong MCC's here. I also don't see one single issue | Judkins (15.7%) | 15.66% | 78.3 | 156.6 | 313.2 | Saddleback (+13.7%) Russek (+9.0%) Olney (-6.0%) Diboll (-4.0%)
CARVER-TINSLEY 138KV | 🟡 Watch | all | HE21, HE20, HE22 | Most shadow pricing seen in HE11 and 12. See this with West wind at 10GW+ coupled with sub 2GW coastal winds | Hamilton (32.3%) | 32.32% | 161.615 | 323.23 | 646.46 | Fort Duncan (+21.0%) Catarina (+9.0%) Russek (-7.0%)
BIG_FOOT-PLEASANT 138KV | 🟡 Watch | summer | HE16, HE13, HE15 | Not that much action since RTC switchover. Too small of shift factors here… | — |  |  |  |  | Fort Duncan (-9.8%) Catarina (-9.2%) Hamilton (-8.8%) Holcomb (-5.3%)
MASN-KATEMCY 69KV | 🟡 Watch | winter | HE19, HE18, HE23 | Affiliated with low west wind and low north wind gen | Junction (25.1%) | 25.1% | 125.5 | 251 | 502 | —
KLNSW-HHSTH 138KV | 🟡 Watch | Spring | HE22, HE23, HE2 | Newer congestion mostly seen in the spring. Esp march and april. Seen all hours but mostly during overnight period. We typically see this congestion when ERCOT wind gen reaches around 24GW+ | — |  |  |  |  | Russek (-5.0%) Judkins (-4.8%) Saddleback (-4.8%) Cisco (-4.0%)
SAMSW-VENSW 345KV | 🟡 Watch | Strongest during winter | HE11, HE12, HE13 | This was strongest in December and Jan, seen in May too. Think its around all seasons. Really no idea what the cause is, look into more, | Diboll (5.3%) | 5.3% | 26.5 | 53 | 106 | Holcomb (-5.6%) Val Verde (-5.6%) Catarina (-5.3%) Olney (+5.0%)
MADDUX-TREADWEL 138KV | 🟡 Watch | Summer and fall | HE17, HE18, HE16 | Haven't seen much post RTC+B should be interesting to look out for. Can't find much of a driver here. | Junction (39.3%) | 39.25% | 196.26 | 392.52 | 785.04 | — |  | Driven by West wind with demand in the east.
PRLSW-CONSW 345KV | 🟡 Watch | Winter and Spring | HE2, HE4, HE1 | Believe we see this congestion with more mild temps, lower loads, and over 8GW+ of west wind generation | Judkins (29.0%) | 29.04% | 145.215 | 290.43 | 580.86 | Saddleback (+23.4%) Russek (+11.1%) Cisco (-5.2%) Olney (-5.0%)
MAXWELL-HAMILTON 138KV | 🟡 Watch | Summer and fall | HE2, HE24, HE1 | Will be interesting to see if this still plays in Post RTC + B. Associated with 13+GW of west wind generation. | Hamilton (23.0%) | 22.98% | 114.885 | 229.77 | 459.54 | Fort Duncan (+14.3%) Russek (-5.0%) Catarina (+5.0%)
LNGSW-CONSW 345KV | 🟡 Watch | Summer | HE1, HE2, HE24 | Haven't seen this one since october 2025. May just be summer congestion. Associated with 10GW+ of west wind gen | Judkins (21.5%) | 21.3% | 106.5 | 213 | 426 | Saddleback (+20.0%) Russek (+8.0%)
SONR-ATSO 69KV | 🟡 Watch | all | HE1, HE3, HE2 | Don't really know what the driver is here. It could be west load surpassing 9GW+ overnight but not sure how common that is. The west wind levels are not very reliable but could be attributed with Low west winds OR high west winds | Russek (5.0%) | 5% | 25 | 50 | 100 | —
LAKENASW-SAMATHIS 69KV | 🟡 Watch | Spring | HE1, HE4, HE24 | See this with low West wind Generation. Seen with sub 6GW of wind generation but gets most active in sub 3GW of west wind generation. Low wind in the Far West is requisite for this to bind. | Russek (7.3%) | 7.252% | 36.26 | 72.52 | 145.04 | — |  | Localized wind and solar production creates tight gradients that have been making this common in lower wind conditions
BRUNI 138KV | 🟡 Watch | All, stronger in winter | HE23, HE22, HE21 | Our shift factors are only like 1% so can't really include this one. Maybe associated with 1.5GW+ of south wind gen | Catarina (1.0%) | 1.044% | 5.22 | 10.44 | 20.88 | —
CRTRVLLE-HILGR 138KV | 🟡 Watch | Fall and winter | HE1, HE2, HE23 | Never rlly seen MCC's over $50 for our west sites so not much to report on here. Driver here is 10GW+ of west wind gen | Judkins (4.0%) | 4% | 20 | 40 | 80 | Saddleback (+4.0%)
ARGYL-LWSVH 138KV | 🟡 Watch | Mostly winter | HE1, HE2, HE24 | Mostly seen in all hour during the winter season. See it when wind patterns reach above 12GW. I would look into this one some more. | Diboll (1.5%) | 1.469% | 7.345 | 14.69 | 29.38 | —
NORTMC-CROSSOVE 138KV | 🟡 Watch | spring and summer | HE19, HE17, HE16 | Above 9.5GW+ of west load. Mostly see it also when west temps reached above 91 degrees which is correlated with load patterns. | Russek (34.2%) | 34.17% | 170.855 | 341.71 | 683.42 | Hamilton (+9.2%) Fort Duncan (+5.7%) | If this is the only binding line on Russek, discharge before solar falls offline. We'll take $100+ MCC here. | High WTX demand (9.6GW is a good threshold) with low WTX wind gives highest shadow pricing
LA_PALMA-HAINE_DR 138KV | 🟡 Watch | spring and summer | HE17, HE16, HE18 | See this congestion with 2GW+ of south wind Gen and 2.5GW+ of coastal wind gen | Val Verde (1.9%) | 1.856% | 9.278 | 18.556 | 37.112 | —
GN-PZ 138KV | 🟡 Watch | Spring | HE16, HE14, HE17 | High coastal wind generation, specifically around 2GW+ | Mainland (18.3%) | 18.32% | 91.61 | 183.22 | 366.44 | —
PILONCIL-NLARSW 138KV | 🟡 Watch | All | All hours, track wind | see this with really low coastal and south winds. Like sub 1GW for each. In the middle of the day, we can see this when coastal and south wind go down to 500MW in both regions (both have less than 500MW of gen) | Holcomb (23.8%) | 23.81% | 119.035 | 238.07 | 476.14 | Catarina (-26.5%) Fort Duncan (-13.0%) Hamilton (-9.4%) Val Verde (+7.6%) | really just important to track the wind. If South gen stays below 500MW and coastal is also below 500MW during middle of day with low west wind, could see this really flare up all day
MV_BURNS-MV_HBRG4 138KV | 🟡 Watch | April | HE17, HE18, HE19 | Common to see when you get 3GW+ of coastal wind levels. Saw most shadow pricing in april of 2026. having 2+GW of south wind stacked also makes the line bind | Val Verde (15.3%) | 15.34% | 76.715 | 153.43 | 306.86 | —
CATARINA-ASHERTON 138KV | 🟡 Watch | Spring | HE22, HE21, HE20 | Have not seen much shadow pricing from here in the past year. We get this congestion with 2.5GW of coastal wind and 2.1GW+ of south wind gen | Hamilton (7.2%) | 7.22% | 36.1 | 72.2 | 144.4 | Catarina (-73.2%) Holcomb (-9.0%) Val Verde (-5.1%)
BR-HOC 138KV | 🟡 Watch | spring (march) | HE16, HE15, HE17 | Common to see with 2.7GW+ of coastal wind gen and 2.5GW of south wind gen. can see in all hours of the day but most common in HE10-18. | Mainland (9.5%) | 9.515% | 47.575 | 95.15 | 190.3 | —
BOW 69KV | 🟡 Watch | Mar-May 2026 | HE9, HE8, HE20 | Pretty new congestion here. Seen march, april and may of 26. We see this congestion with high system-wide winds. Around like 20GW+ of wind gen | — |  |  |  |  | Olney (-5.0%)
CMNSW-CMNTP 138KV | 🟡 Watch | all | HE17, HE19, HE18 | Get this congestion when coastal winds surpass 2.7GW+ of coastal gen. When system wide wind gen reaches to 20GW+ is where we get the best shadow pricing. Don't get much pricing from here though with low shift factors. Far West Solar is a significant source-side driver. When coupled with wind and high Dallas temps, this will continue to bind. | Cisco (5.0%) | 5% | 25 | 50 | 100 | —
UVALDE-READING 138KV | 🟡 Watch | Summer | HE19, HE18, HE17 | Haven't seen post RTC. No good positive shift factor but hamilton has strong negative. Can't find a specific driver but 19GW+ of south load could be a driver with low south wind | — |  |  |  |  | Hamilton (-20.5%) Fort Duncan (-8.9%) Catarina (-8.1%)
WOLFCAMP-SANTARIT 138KV | 🟡 Watch | Outage/Event | HE17, HE16, HE19 | No specific driver I can find here. Russek has a 32% shift factor here. High temps also tend to flair up this line. Only saw for 2 days in April | Russek (31.7%) | 31.74% | 158.695 | 317.39 | 634.78 | —
LHSES-PRCSW 138KV | 🟡 Watch | Fall of 2025 | HE20, HE19, HE17 | Skip this one. Only -5% shift factor here at North sites | — |  |  |  |  | Diboll (-5.0%)
LAREDO-DEL_MAR 138KV | 🟡 Watch | Summer 2025 | HE23, HE24, HE22 | Will be interesting to see if we see this congestion this summer. Not very strong pricing here though. Skip | Holcomb (6.0%) | 6% | 30 | 60 | 120 | —
COLETO CREEK-VICTORIA | 🟡 Watch | Spring 26 | HE20, HE22, HE21 | Strong hours are HE20-1 but seen across all hours. This seems to be all coastal wind generated. When we get over 2.4GW of coastal wind gen, theres a good change we'll see this. Strongest shadow pricing has come from coastal wind at 3GW+ | — |  |  |  |  | Val Verde (-9.2%)
FMRVL-RYSSW 345KV | 🟡 Watch |  | HE17, HE16, HE15 | Dibol only has a 6% shift factor here but seen shadow pricing in the thousands. Only saw decent shadow pricing for one day. Delete | Diboll (5.2%) | 5.227% | 26.135 | 52.27 | 104.54 | Olney (-3.4%)
⚫ LOW PRIORITY — Skip or Outage-Only
LOBO-LARDVNTH 138KV | ⚫ Low Priority | Feb and March | HE22, HE19, HE21 | Newer Congestion (First seen Feb 2026). Can be seen at all times throughout the day but mostly 17-3. Correlates with 2.5GW+ of south wind or 2.8GW+ of coastal wind. Maybe was also outage driven bc we haven't seen it since march. | Holcomb (32.4%) | 32.39% | 161.93 | 323.86 | 647.72 | Catarina (+21.8%) Hamilton (+7.0%) Fort Duncan (+7.0%) Val Verde (-7.0%)
BCESW-SNDSW 345KV | ⚫ Low Priority | Fall and Spring | HE17, HE18, HE16 | Not much activity here during summer and winter. Also see this one when south wind is sub 1GW. Consistent factor also seems to be days of strong south load (15GW+) during the solar window | Holcomb (11.0%) | 11% | 55 | 110 | 220 | Val Verde (+11.0%) Catarina (+10.0%) Fort Duncan (+9.0%) Diboll (-7.4%)
LARDVNTH-LASCRUCE 138KV | ⚫ Low Priority | Big summer cong | HE20, HE21, HE22 | Historically this congestion was seen over the summer but don't have any real shadow pricing since september of 2025. The main driver of this congestion was elevated STX wind patterns overnight. | Holcomb (29.7%) | 29.74% | 148.68 | 297.36 | 594.72 | Catarina (+17.9%) Val Verde (-7.9%) Hamilton (+6.2%) |  | the absence of binding intervals for this exact line in the past 90 days is consistent with a conductor upgrade that began construction in 2024 on this specific segment (congestion may be dead)
LASCRUCE-MILO 138KV | ⚫ Low Priority | Winter | HE20, HE19, HE21 | south AND coastal wind gen at 2GW+ | Holcomb (28.0%) | 28.02% | 140.125 | 280.25 | 560.5 | Catarina (+17.3%) Fort Duncan (+9.6%) Val Verde (-8.0%) Hamilton (+7.0%) |  | AEP Texas's North Laredo Transmission Improvements Project factsheet explicitly lists the Milo – Las Cruces transmission line as one of the segments being rebuilt
STP-ELMCREEK 345KV | ⚫ Low Priority | Nov, Dec, Jan | HE22, HE21, HE23 | Mostly correlated with low renewable generation on the grid. See the congestion overnight with low (sub 8gw) of wind gen on the grid | Catarina (8.0%) | 8% | 40 | 80 | 160 | Mainland (-9.0%) Holcomb (+7.9%) Fort Duncan (+7.5%) Hamilton (+6.7%)
VEALMOOR-KOCHTAP 138KV | ⚫ Low Priority | All but gone now | HE23, HE24, HE22 | Haven't seen at all in RTC. Look a pic on the right. This congestion was sooo prevelent before RTC, generating just below $300,000 (in $/mwh) in shadow pricing from May-Nov 2025 and now is completely gone | Judkins (5.2%) | 5.24% | 26.2 | 52.4 | 104.8 | Saddleback (+4.5%)
SNDHT-WLFSW 138KV | ⚫ Low Priority | Outage/Event | HE4, HE2, HE1 | Nothing in RTC so far. Saw strong in July which could've made this congestion outage driven | Saddleback (7.0%) | 7% | 35 | 70 | 140 | Judkins (-44.9%)
WCRYSTS-CARIZOS 69KV | ⚫ Low Priority | x | HE7, HE8, HE5 | This is just completely outage drive. Saw for 5 days in Feb. No other driver seen | Fort Duncan (19.0%) | 19% | 95 | 190 | 380 | Hamilton (+12.6%) Catarina (-5.0%)
JEWET-BBSES 345KV | ⚫ Low Priority | x | HE21, HE20, HE8 | Also outage driven. Saw for 8 days in Feb at random times. Strong in HE 9 though | Diboll (12.9%) | 12.87% | 64.37 | 128.74 | 257.48 | Mainland (-10.0%) Olney (+8.3%) Cisco (+6.8%) Holcomb (-5.0%)
ABNTHWST 138KV | ⚫ Low Priority | x | HE17, HE16, HE18 | Saw this one hit hard during Fern. Associated with high north load during the down ramp. The days we saw this congestion reach shadow prices of $200 $/mwh, North load was getting up to 24GW | Cisco (13.9%) | 13.95% | 69.735 | 139.47 | 278.94 | —
KLNSW-STAGE 138KV | ⚫ Low Priority | March 17-31 | HE22, HE23, HE24 | Outage driven here. Not strong enough shift factors to to make a huge difference | Val Verde (2.1%) | 2.1% | 10.5 | 21 | 42 | Russek (-4.0%) Judkins (-4.0%) Saddleback (-4.0%) Cisco (-3.0%)
HAMILTON-MAVERICK 138KV | ⚫ Low Priority | x | HE17, HE20, HE21 | I think this is associated with high west winds and low south wind but not rlly sure. May have to dig deeper here | Fort Duncan (19.6%) | 19.61% | 98.06 | 196.12 | 392.24 | Hamilton (-56.0%) Catarina (+7.2%)
HCKSW 1KV | ⚫ Low Priority | April 9th-14th | HE19, HE21, HE20 | Completely outage driven. Super weak shift factor here at dibol for 1% | — |  |  |  |  | Judkins (-4.0%) Saddleback (-4.0%) Russek (-3.5%) Olney (-3.0%)
PILONCIL-CATARINA 138KV | ⚫ Low Priority | x | HE22, HE20, HE21 | Only seen congestion once here on May 27th 2025. really has to just be outage driven considering we only saw it for 1 day | Catarina (33.7%) | 33.7% | 168.5 | 337 | 674 | Holcomb (-9.8%)
W_BATESV-UVALDE 138KV | ⚫ Low Priority | all | HE22, HE4, HE21 | Ft Duncan and Hamilton have 20% shift factors here w/ cat on the neg side. Could be related to low north wind output, don't think it has anything to do with load and low NTX wind gen is the only consistent factor seen. | Fort Duncan (30.0%) | 29.99% | 149.965 | 299.93 | 599.86 | Hamilton (+27.5%) Catarina (-15.0%) Holcomb (-6.0%)
VALEXP | ⚫ Low Priority | Mostly winter | HE4, HE3, HE5 | Not relly sure what the driver is here. This is a massive base case line in STX going from Edinburg to around Port Aransas. Only thing that correlates is low North wind gen and sub 5GW of WTX gen but that doesn't make much sense considering the location | — |  |  |  |  | Val Verde (-98.2%)
MDO-PHR 345KV | ⚫ Low Priority | Summer | HE16, HE14, HE15 | See a little show up in May in april of this year. Was common last summer. Not sure exactly what the driving factor is here. Houston load could be the driving factor here, tends to pop up when we reach 20GW of load in houston. | — |  |  |  |  | Val Verde (-10.0%) Holcomb (-9.6%) Catarina (-9.1%) Fort Duncan (-7.7%)
FTSSW-VENSW 345KV | ⚫ Low Priority | x | HE16, HE15, HE17 | Seems like a pretty big Pre-RTC congestion commoner. Only seen once post RTC swithover on Jan 5th. Pic on right. Strong driver was days of high loads, esp the north reaching to 24 +GW of load. | — |  |  |  |  | Holcomb (-6.0%) Val Verde (-6.0%) Catarina (-5.7%) Fort Duncan (-4.7%)
NVKSW-ANARN 69KV | ⚫ Low Priority | x | HE18, HE17, HE16 | Strongest during solar window. No direct season associated, pretty sporadic. Only driver I can find is when north wind levels reach to 1.8GW+, see this one mostly in shoulder seasons when system wide wind levels get to 17GW+. High North winds and panhandle winds are mostly the answer to this congestion | Olney (47.6%) | 47.6% | 238 | 476 | 952 | —
OZONA-MIDW 69KV | ⚫ Low Priority | Sporadic | HE16, HE15, HE13 | My theory is low wtx load paired with low wtx wind gen but could also be outage driven in the area bc these price pops are sporadic. | Russek (6.0%) | 6% | 30 | 60 | 120 | —
TMPSW-TMPCR 345KV | ⚫ Low Priority | x | HE21, HE20, HE4 | This is completely outage drive. Only seen one day and we don't have much of a shift factor. Delete this | Diboll (8.2%) | 8.2% | 41 | 82 | 164 | Holcomb (-10.0%) Val Verde (-9.9%) Catarina (-9.3%) Olney (+8.1%)
ZEN-THW 345KV | ⚫ Low Priority | x | HE15, HE14, HE16 | Don't get much shadow pricing here. Delete this | Mainland (11.1%) | 12.78% | 63.91 | 127.82 | 255.64 | Cisco (-84.0%) Diboll (-10.0%) Olney (-8.0%) Judkins (-7.7%)
DOW-OAS 345KV | ⚫ Low Priority | x | HE14, HE16, HE15 | This could be outage driven based on its spiradic history. See the highest shadow pricing with coastal wind levels at 2.5GW+ | Mainland (17.6%) | 17.58% | 87.9 | 175.8 | 351.6 | Val Verde (-8.2%) Holcomb (-7.7%) Catarina (-7.2%) Fort Duncan (-6.0%)
MAVERICK-HAMILTON 138KV | ⚫ Low Priority | x | HE2, HE4, HE3 | Outage driven line. Saw in Jan | Hamilton (40.6%) | 40.61% | 203.025 | 406.05 | 812.1 | Fort Duncan (-25.8%) Catarina (-8.9%) Russek (+5.3%)
SNDSW-AUSTRO 345KV | ⚫ Low Priority | Spring | HE16, HE17, HE15 | Our south assets have strong shift factors here at around 15%. Shadow pricing has been very weak only reaching $237 max which is when stx load has reached 17GW. | Holcomb (15.0%) | 15.04% | 75.21 | 150.42 | 300.84 | Val Verde (+14.8%) Catarina (+14.1%) Fort Duncan (+11.4%) Olney (-9.9%)
GANSO-MAVERICK 138KV | ⚫ Low Priority | x | HE4, HE6, HE5 | Pretty common to see when you get 2GW+ of wind gen in the coast. Prob has to do more with outages here during the time seen really only one day in january | Hamilton (40.2%) | 40.19% | 200.965 | 401.93 | 803.86 | Catarina (-9.2%) Holcomb (-4.4%)
RIOHONDO-MV_BURNS 138KV | ⚫ Low Priority | July and Aug 2025 | HE18, HE17, HE19 | Haven't seen at all in RTC. Should be interesting to see, this is correlated with high south loads, specifically 19GW+ with over 2GW+ of stx wind gen and 2.5GW+ of coastal gen | Val Verde (19.8%) | 19.76% | 98.8 | 197.6 | 395.2 | —
MADDUX-SAPOWER 138KV | ⚫ Low Priority | x | HE7, HE8, HE6 | Skip this one. Super low shadow price (not even above $150) | — |  |  |  |  | Junction (-33.6%) Hamilton (-11.7%) Fort Duncan (-7.4%) Russek (-7.0%)
MILLER-HENLY 138KV | ⚫ Low Priority | x | HE17, HE18, HE19 | Skip this one. Completely outage driven in sept of 25 | — |  |  |  |  | Junction (-11.0%)
ODESA-ODNTH 138KV | ⚫ Low Priority | winter | HE23, HE5, HE22 | See this in the winter with 10GW+ of wtx wind gen | Saddleback (8.0%) | 8% | 40 | 80 | 160 | —
CPSES-MBDSW 345KV | ⚫ Low Priority | outage | HE20, HE1, HE7 | Mostly outage driven here. Saw in nov and 2 days in april. Also need like 20GW+ of wind gen online. Prob common to see when WESTEX is flaring up | — |  |  |  |  | Russek (-6.0%) Judkins (-5.9%) Saddleback (-5.8%) Junction (-4.5%)
KENDAL-BERGHE 345KV | ⚫ Low Priority | x | HE14, HE13, HE12 | See this with like 13GW+ of west wind. Haven't seen a shadow price above $150 so don't look too deep into. Can see in all hours but most common in HE11-17 | Val Verde (10.3%) | 10.35% | 51.745 | 103.49 | 206.98 | Junction (-15.7%) Saddleback (-14.5%) Russek (-13.8%) Judkins (-13.2%)
DOWNIES-MOORE 138KV | ⚫ Low Priority | Summer 25 | HE14, HE16, HE15 | delete too low shift factor. Was all outage driven in may 25 | — |  |  |  |  | Fort Duncan (-18.2%) Hamilton (-15.5%) Catarina (-6.0%)
TNFXTAIL-FLAT_TOP 138KV | ⚫ Low Priority | Fall 25 | HE17, HE16, HE15 | Good shift factors on WTX sites but never get much shadow pricing. See this when WTX wind goes sub 5GW only get like max $350 of shadow pricing | Saddleback (31.3%) | 31.33% | 156.66 | 313.32 | 626.64 | —
EXCSW-RNKSW 345KV | ⚫ Low Priority | x | HE20, HE21, HE19 | Theory here is also high wind generation throughout ERCOT. Too low of shift factors | Diboll (4.4%) | 4.448% | 22.24 | 44.48 | 88.96 | Olney (-6.8%) Cisco (-6.6%) Judkins (-6.4%) Saddleback (-6.2%)
SAMSW-FVLSW 345KV | ⚫ Low Priority | x | HE12, HE11, HE10 | Skip shadow pricing doesn't go above $160 | Olney (5.5%) | 5.485% | 27.425 | 54.85 | 109.7 | Val Verde (-5.9%) Holcomb (-5.8%) Catarina (-5.6%) Fort Duncan (-4.8%)
TNP_ONE-TOKSW 345KV | ⚫ Low Priority | x | HE15, HE14, HE13 | Skip shadow pricing doesn't exceed 250 | Mainland (6.6%) | 6.594% | 32.97 | 65.94 | 131.88 | Junction (-7.5%) Diboll (+6.4%) Catarina (-6.4%) Holcomb (-6.2%)
GT-BG 138KV | ⚫ Low Priority | All in April 2026 | HE17, HE16, HE12 | Probably all outage driven for the month of april. Best shadow pricing seen at 2.6GW+ of coastal wind gen. | Mainland (14.3%) | 14.26% | 71.285 | 142.57 | 285.14 | —
I_KALO | ⚫ Low Priority | x | HE13, HE15, HE14 | My theory here is low load days with very high renewables online. | Val Verde (25.7%) | 25.69% | 128.455 | 256.91 | 513.82 | Holcomb (+6.5%)
BLESSING 345KV | ⚫ Low Priority | x | HE22, HE9, HE7 | This one I can't really figure out the driver for. Shadow pricing can get high here but we don't have super strong shift factors. I deleted the previous Blessings 345 line due to low shift factors but was a very common congestion to see | Val Verde (6.3%) | 6.3% | 31.5 | 63 | 126 | Holcomb (+4.1%)
SANA 138KV | ⚫ Low Priority | Sporadic | HE6, HE5, HE4 | Will only see this one in one day increments, never see two days in a row. Haven't seen any of this post RTC but could just be driven from other transmission outages in the area. When it pops up there is sub 1GW of North wind. Have very low sf here though | Cisco (4.0%) | 4% | 20 | 40 | 80 | —
ELGISW-BUTLER 138KV | ⚫ Low Priority | x | HE18, HE16, HE17 | all outage driven | Val Verde (4.6%) | 4.6% | 23 | 46 | 92 | Holcomb (+4.5%) Catarina (+4.2%)
ESTLD-MRVLY 69KV | ⚫ Low Priority | x | HE13, HE8, HE9 | I have absolutely no idea what is causing this congestion. Only seen real shadow pricing for 3 days the past year. Skip this. | Olney (5.3%) | 5.3% | 26.5 | 53 | 106 | Cisco (-4.5%)
HOLMAN-CISTERN 345KV | ⚫ Low Priority | Outage/Event | HE21, HE22, HE4 | all outage driven | Junction (6.5%) | 6.49% | 32.45 | 64.9 | 129.8 | Mainland (-7.1%) Fort Duncan (+5.6%) Catarina (+5.6%) Hamilton (+5.4%)
YELWJCKT-HEXT 69KV | ⚫ Low Priority | x | HE14, HE17, HE12 | Low shift factors here. Only 5% at junction. Only saw 2 days of real shadow pricing in Jan of 2026. Skip this one | Junction (5.9%) | 5.9% | 29.5 | 59 | 118 | —
CRD 345KV | ⚫ Low Priority | x | HE22, HE2, HE1 | all outage driven and russek has the strongest shift factor of 6%. | Cisco (6.0%) | 6% | 30 | 60 | 120 | —
BRACKETT-ESCONDID 138KV | ⚫ Low Priority | x | HE18, HE17, HE16 | Haven't seen any congestion here since July 2025 | Catarina (10.1%) | 10.13% | 50.665 | 101.33 | 202.66 | Hamilton (-32.3%) Russek (-4.2%) Holcomb (+4.1%)
BANDER-MASOCR 138KV | ⚫ Low Priority | outage | HE16, HE19, HE18 | all outage driven. | — |  |  |  |  | Junction (-8.0%)
CNRSW 345KV | ⚫ Low Priority | Fall 25 | HE15, HE14, HE16 | We see this pricing with extremely low NTX wind generation, especially when it hits that 200mw number. Only seen max shadow price of $250 so not much of an impact. | — |  |  |  |  | Diboll (-14.1%)
EINSTEIN-CRTRVLLE 138KV | ⚫ Low Priority | x | HE8, HE7, HE9 | Delete this one. Too small shift factor and only $40 mcc for Judkins at max shadow pricing | Judkins (4.8%) | 4.849% | 24.245 | 48.49 | 96.98 | Saddleback (+3.8%)
🆕 NEW
PEARSALL-POTEETS 69KV | 🆕 New | Summer | HE17, HE18, HE16 |  | Poteet (39.1%) | 39.1% | 195.515 | 391.03 | 782.06 | None significant (<2%)
BCPSW-AZLES 138KV | 🆕 New |  | HE18, HE19, HE17 |  | Mineral Wells (22.5%) | 22.5% | 195.515 | 225 | 450 | Olney (+4.0%) Cisco (+3.0%)
MV_BHBRG4-MV_WESL$ 138kV | New | Summer | HE 16-19 | Long term: South wind is the main source of this congestion but it really just shows up with high demand in the summer (18 + of STX load) and will stick around all summer. The time window is all that really needs to be considered. This congestion really started up in May. | Val Verde (15%) | 15% |  |  |  | Falfurrias (3%) Holcomb (1%) | Hold if south wind is increasing and congestion shows up earlier than designated time window but most of time it's a rip it when you see it. Rip before it falls off. HE16-19 strongest shadow prices. Rip it before HE20 | Always drops out before HE20!! Outage from AJO_REFORZ21_LN also is main cause. This congestion binds 50% of the time when south load reaches 22GW+ and seasonally starts when south loads start reaching 18GW. South wind also major contributor
POTEET-OAKS 69kV | New |  | HE16-19 | GR_Coastal above ~1,900-2,000 MW AND SCEN (south central) load above 14,000 MW, in the 14:00-19:00 window. | Poteet (-44%) | -44% |  |  |  |  | Hold if south wind is increasing. Rip before solar falls out. Hold charge room if we're expecting congestion | Also need DEVINE-BIGFOOT in outage for this congestion. Window can be from 2pm-7pm. Best thresehold I have is 800MW of south wind and 14GW of south central weatherzone load.
ORNGROV-ORNGROC | New |  | HE16-19 | This congestion also stems from STX wind generation. Don't know where the wind gen is coming from exactly (some local wind farm) but when you see this congestion pop up, know it is from the stx wind output | Tynan (17%) | 17% |  |  |  |  | Rip it when you see it
ORNGROV-SNDIEGS 69kV | NEW | outage driven | HE14-16 | This congestion is driven by a line outage from ALICE_KINGSV. Rip falfurrias when you see this congestion and tynan will see a charge window. The ALICE_KINGSV line normally goes into outage in the morning, then comes back online. Just have to check outage scheduler to see when the line is coming back online. | Fafurrias (5%) Tynan (-5%) | [5 empty] | Rip Falfurrias when it pops up | Main drivers with the outage for this congestion is seeing south wind go below 300MW during the solar window.

## 🧮 MCC Calculator
REAL-TIME MCC CALCULATOR — Shadow Price × Shift Factor = MCC at Node
Enter the real-time shadow price ($/MWh) you see for a line → MCC at each site auto-calculates = SF × Shadow Price
ENTER SHADOW PRICE ($/MWh): |  |  | 197 | ← Change this value to see real-time MCC impact at each site
Line / Constraint | Priority | Prim. Node | SF (%) | Russek | Catarina | Holcomb | Hamilton | Fort Duncan | Junction | Judkins | Saddleback | Val Verde | Mainland | Cisco | Diboll | Olney
TWINBU-HARGROVE 138KV | 🟢 Active | Russek (31.7%) | 31.66% | 62.38 | — | — | 13.3763 | 8.6404 | — | 3.5086 | 4.8955 | — | — | — | — | —
LARDVNTH-LASCRUCE 138KV | 🟢 Active | Holcomb (29.7%) | 29.74% | 1.97 | 35.2335 | 58.5799 | 12.1313 | — | — | — | — | -15.563 | — | — | — | —
FORTMA-YELWJCKT 138KV | 🟢 Active | Junction (50.0%) | 50% | 6.304 | — | — | — | — | 98.5 | 3.94 | 3.94 | — | — | — | — | —
STP-ELMCREEK 345KV | 🟢 Active | Catarina (8.0%) | 8% | 8.274 | 15.76 | 15.563 | 13.199 | 14.775 | 11.426 | 7.289 | 7.683 | 10.244 | -17.73 | 4.531 | — | 3.94
TREADWEL-YELWJCKT 138KV | 🟢 Active | Junction (46.8%) | 46.76% | — | 2.955 | 2.955 | — | — | 92.1074 | — | — | 2.955 | — | — | — | —
LASCRUCE-MILO 138KV | 🟢 Active | Holcomb (28.0%) | 28.02% | — | 34.0042 | 55.2092 | 13.79 | 19.0066 | — | — | — | -15.76 | — | — | — | —
WESTEX | 🟢 Active | Diboll (19.4%) | 19.4% | -130.02 | 14.8026 | 25.742 | -45.31 | -13.79 | -59.1 | -141.446 | -141.052 | 30.204 | 35.3359 | -101.061 | 38.2101 | -109.926
LNGSW-PRLSW 345KV | 🟢 Active | Judkins (21.3%) | 21.33% | 13.79 | -3.94 | -3.94 | 3.94 | 3.94 | -3.94 | 42.0181 | 40.2116 | -3.94 | -3.94 | -3.94 | -3.94 | -3.94
E_PASP | 🟢 Active | Junction (4.0%) | 4% | — | -16.8553 | -27.1427 | — | — | 7.88 | — | — | -38.6613 | — | — | — | —
NLARSW-PILONCIL 138KV | 🟢 Active | Catarina (26.0%) | 26% | — | 51.22 | -17.73 | 17.007 | 23.64 | — | — | — | -11.82 | — | — | — | —
MGSES-CATSW 345KV | 🟢 Active | Judkins (30.0%) | 30% | 19.7 | — | — | — | — | — | 59.1 | 53.2629 | — | -9.85 | -15.76 | -11.82 | -13.79
LOBO-LARDVNTH 138KV | 🟢 Active | Holcomb (32.4%) | 32.39% | — | 42.9775 | 63.8004 | 13.79 | 13.79 | — | — | — | -13.79 | — | — | — | —
ESCONDID-GANSO 138KV | 🟢 Active | Hamilton (40.4%) | 40.35% | 9.85 | -18.518 | -8.668 | 79.4895 | -51.4958 | — | — | — | — | — | — | — | —
BCESW-SNDSW 345KV | 🟢 Active | Holcomb (11.0%) | 11% | — | 19.7 | 21.67 | 13.79 | 17.73 | — | -7.88 | -7.88 | 21.67 | — | -11.82 | -14.578 | -12.805
LNGSW-CONSW 345KV | 🟢 Active | Judkins (21.3%) | 21.3% | 15.76 | — | — | — | — | — | 41.961 | 39.4 | — | — | — | — | —
YELWJCKT-FORTMA 138KV | 🟢 Active | — |  | — | — | — | — | — | -98.5 | — | — | — | — | — | — | —
Legend: | 🟢 Active = detailed MCC analysis completed | — |  | — | — | — | — | — | — | — | — | — | — | — | — | —
ASHERTON-CATARINA 138KV | 🟡 Watch | Catarina (77.0%) | 76.98% | — | 151.6545 | 33.9727 | -17.73 | -22.852 | — | — | — | — | — | — | — | —
MRVLY-ESTLD 69KV | 🟡 Watch | Cisco (17.3%) | 17.35% | — | — | — | — | — | — | — | — | — | — | 34.1756 | — | —
STP-WAP 345KV | 🟡 Watch | Mainland (9.6%) | 9.57% | — | -16.745 | -18.6401 | -9.85 | -13.79 | — | — | — | -22.2531 | 18.8529 | — | — | —
PALOUSE-WOLFCAMP 138KV | 🟡 Watch | Russek (30.6%) | 30.57% | 60.2209 | — | — | — | — | — | — | — | — | — | — | — | —
LPLMK-LPLNE 115KV | 🟡 Watch | Judkins (1.6%) | 1.594% | 2.0567 | — | — | 1.1308 | — | — | 3.1402 | 2.9294 | — | — | — | — | —
CRDSW-OLNEY 69KV | 🟡 Watch | Olney (78.7%) | 78.68% | — | — | — | — | — | — | — | — | — | — | — | — | 155.0035
HONDOCK-DEVINESW 69KV | 🟡 Watch | — |  | — | -9.85 | — | -11.82 | -12.608 | — | — | — | — | — | — | — | —
I_FW_N | 🟡 Watch | Judkins (15.7%) | 15.66% | 17.73 | — | — | — | — | — | 30.8502 | 27.0678 | — | — | — | -7.88 | -11.82
CARVER-TINSLEY 138KV | 🟡 Watch | Hamilton (32.3%) | 32.32% | -13.79 | 17.73 | — | 63.6763 | 41.37 | — | — | — | — | — | — | — | —
BIG_FOOT-PLEASANT 138KV | 🟡 Watch | — |  | — | -18.124 | -10.5198 | -17.336 | -19.306 | — | — | — | — | — | — | — | —
MASN-KATEMCY 69KV | 🟡 Watch | Junction (25.1%) | 25.1% | — | — | — | — | — | 49.447 | — | — | — | — | — | — | —
KLNSW-HHSTH 138KV | 🟡 Watch | — |  | -9.85 | — | — | — | — | — | -9.456 | -9.456 | — | — | -7.88 | — | —
SAMSW-VENSW 345KV | 🟡 Watch | Diboll (5.3%) | 5.3% | — | -10.441 | -11.032 | — | -8.668 | — | — | — | -11.032 | -7.88 | — | 10.441 | 9.85
MADDUX-TREADWEL 138KV | 🟡 Watch | Junction (39.3%) | 39.25% | — | — | — | — | — | 77.3264 | — | — | — | — | — | — | —
PRLSW-CONSW 345KV | 🟡 Watch | Judkins (29.0%) | 29.04% | 21.8197 | — | — | 9.0226 | — | — | 57.2147 | 46.0389 | — | — | -10.3425 | -8.077 | -9.85
MAXWELL-HAMILTON 138KV | 🟡 Watch | Hamilton (23.0%) | 22.98% | -9.85 | 9.85 | — | 45.2647 | 28.2104 | — | — | — | — | — | — | — | —
LNGSW-CONSW 345KV | 🟡 Watch | Judkins (21.5%) | 21.3% | 15.76 | — | — | — | — | — | 41.961 | 39.4 | — | — | — | — | —
SONR-ATSO 69KV | 🟡 Watch | Russek (5.0%) | 5% | 9.85 | — | — | 2.758 | — | — | — | — | — | — | — | — | —
LAKENASW-SAMATHIS 69KV | 🟡 Watch | Russek (7.3%) | 7.252% | 14.2864 | — | — | — | — | — | — | — | — | — | — | — | —
BRUNI 138KV | 🟡 Watch | Catarina (1.0%) | 1.044% | — | 2.0567 | — | — | 2.0567 | — | — | — | — | — | — | — | —
CRTRVLLE-HILGR 138KV | 🟡 Watch | Judkins (4.0%) | 4% | — | — | — | — | — | — | 7.88 | 7.88 | — | — | — | — | —
ARGYL-LWSVH 138KV | 🟡 Watch | Diboll (1.5%) | 1.469% | — | — | — | — | — | — | — | — | — | — | — | 2.8939 | —
NORTMC-CROSSOVE 138KV | 🟡 Watch | Russek (34.2%) | 34.17% | 67.3169 | — | — | 18.0984 | 11.229 | — | -5.516 | -4.6295 | — | — | — | — | —
LA_PALMA-HAINE_DR 138KV | 🟡 Watch | Val Verde (1.9%) | 1.856% | — | — | 2.2419 | — | — | — | — | — | 3.6563 | — | — | — | —
GN-PZ 138KV | 🟡 Watch | Mainland (18.3%) | 18.32% | — | — | — | — | — | — | — | — | — | 36.0943 | — | — | —
PILONCIL-NLARSW 138KV | 🟡 Watch | Holcomb (23.8%) | 23.81% | — | -52.1676 | 46.8998 | -18.6067 | -25.5371 | — | — | — | 14.972 | — | — | — | —
MV_BURNS-MV_HBRG4 138KV | 🟡 Watch | Val Verde (15.3%) | 15.34% | — | — | — | — | — | — | — | — | 30.2257 | — | — | — | —
CATARINA-ASHERTON 138KV | 🟡 Watch | Hamilton (7.2%) | 7.22% | — | -144.204 | -17.7556 | 14.2234 | — | — | — | — | -10.1258 | — | — | — | —
BR-HOC 138KV | 🟡 Watch | Mainland (9.5%) | 9.515% | — | — | — | — | — | — | — | — | — | 18.7446 | — | — | —
BOW 69KV | 🟡 Watch | — |  | — | — | — | — | — | — | — | — | — | — | — | — | -9.85
MCCAMY | 🟡 Watch | — |  | -48.5743 | — | — | -22.2255 | -13.5418 | — | — | — | — | — | — | — | —
CMNSW-CMNTP 138KV | 🟡 Watch | Cisco (5.0%) | 5% | — | — | — | — | — | — | — | — | — | — | 9.85 | — | —
UVALDE-READING 138KV | 🟡 Watch | — |  | — | -15.9432 | — | -40.3141 | -17.6019 | — | — | — | — | — | — | — | —
WOLFCAMP-SANTARIT 138KV | 🟡 Watch | Russek (31.7%) | 31.74% | 62.5258 | — | — | — | — | — | — | — | — | — | — | — | —
LHSES-PRCSW 138KV | 🟡 Watch | — |  | — | — | — | — | — | — | — | — | — | — | — | -9.85 | —
LAREDO-DEL_MAR 138KV | 🟡 Watch | Holcomb (6.0%) | 6% | — | — | 11.82 | — | — | — | — | — | — | — | — | — | —
COLETO CREEK-VICTORIA | 🟡 Watch | — |  | — | — | — | — | — | — | — | — | -18.0649 | — | — | — | —
FMRVL-RYSSW 345KV | 🟡 Watch | Diboll (5.2%) | 5.227% | — | — | — | — | — | — | — | — | — | — | — | 10.2972 | -6.7473
NOTE: Negative MCC values (in red) indicate the node BENEFITS from the constraint — congestion lowers prices at that node. Positive MCC = congestion increases prices at your node.

## ☀️ Summer
SUMMER CONGESTION PLAYBOOK ¦ Jun – Aug
Summer peak load. South/coastal wind gen key driver. Monitor west load 9GW+.
Line / Constraint | Priority | Peak HE (Best Hours) | Driver / Trigger | Primary Node | SF (%) | MCC @ $500 SP | MCC @ $1000 SP | Discharge Guidance | Hold Strategy? | Key Gen Level Threshold | Operator Notes
🟢 ACTIVE LINES — Priority Targets for Jun – Aug
TWINBU-HARGROVE 138KV | 🟢 Active | HE5, HE6, HE4 | West wind sub 5GW is when we see it strongest. Possible to see around sub 8Gw | Russek (31.7%) | 31.66% | 158.325 | 316.65 | Discharge at SP ≥ $300-500/MWh (MCC $158+ at primary node) | Yes — hold for higher pricing overnight |  | Willing to sit on high pricing HE20-24.
LARDVNTH-LASCRUCE 138KV | 🟢 Active | HE20, HE21, HE22 | Congestion should start popping up soon historically. See when south wind gen gets up to 2GW+ and coastal winds at 2GW+ | Holcomb (29.7%) | 29.74% | 148.68 | 297.36 | Discharge at SP ≥ $300-500/MWh (MCC $149+ at primary node) | Monitor trend; discharge on confirmed ramp
FORTMA-YELWJCKT 138KV | 🟢 Active | HE21, HE20, HE23 | Mostly seen overnight. Correlated when west dips below coastal wind generation. West wind gen generally has to be below 3GW | Junction (50.0%) | 50% | 250 | 500 | Discharge at SP ≥ $300-500/MWh (MCC $250+ at primary node) | Monitor trend; discharge on confirmed ramp
TREADWEL-YELWJCKT 138KV | 🟢 Active | HE17, HE18, HE19 | Haven't seen any of this congestion since the RTC switch. Seen when west load reached 9GW+, which we've seen in May but didn't see any congestion. This one may be gone but worth diving into more | Junction (46.8%) | 46.76% | 233.775 | 467.55 | Discharge at SP ≥ $300-500/MWh (MCC $234+ at primary node) | Monitor trend; discharge on confirmed ramp
WESTEX | 🟢 Active | HE20, HE19, HE12 | See flare up in days of high renewable generation. Seen in all hours of the day but most common during solar ramps or when west Gen reaches above 15GW overnight. | Diboll (19.4%) | 19.4% | 96.98 | 193.96 | Discharge at SP ≥ $500-800/MWh (MCC $97+ at node) | Monitor trend; discharge on confirmed ramp
LNGSW-PRLSW 345KV | 🟢 Active | HE1, HE2, HE24 | This congestion is seem mostly overnight. Main driver on this line is when we see west wind gen reach above 10GW. | Judkins (21.3%) | 21.33% | 106.645 | 213.29 | Discharge at SP ≥ $300-500/MWh (MCC $107+ at primary node) | Monitor trend; discharge on confirmed ramp
E_PASP | 🟢 Active | HE20, HE19, HE18 | This sends Val Verde negative. Strongest during down ramps best theory for congestion here is when south load reaches 18GW+. | Junction (4.0%) | 4% | 20 | 40 | Only strong pricing (SP>$2000) creates meaningful MCC | Monitor trend; discharge on confirmed ramp
NLARSW-PILONCIL 138KV | 🟢 Active | HE24, HE1, HE2 | This is a newer congestion… started in Nov 2025. see this congestion with coastal wind gen at 2.5GW+. Same with south wind | Catarina (26.0%) | 26% | 130 | 260 | Discharge at SP ≥ $300-500/MWh (MCC $130+ at primary node) | Monitor trend; discharge on confirmed ramp
MGSES-CATSW 345KV | 🟢 Active | HE23, HE19, HE20 | Newer congestion (start Nov 2025). Mostly see this congestion with cooler weather in the west creating higher load levels (9gw+) and wind sub 8GW. This ould be the inbalance of demand and wind gen. look into that also maybe coastal wind gen | Judkins (30.0%) | 30% | 150 | 300 | Discharge at SP ≥ $300-500/MWh (MCC $150+ at primary node) | Monitor trend; discharge on confirmed ramp
ESCONDID-GANSO 138KV | 🟢 Active | HE8, HE9, HE1 | HE 10 saw the most shadow pricing but morning all around get best pricing. We see this congestion with low wind generation online, especially the west goin sub 3GW paired with WTX seeing a 9GW+ load | Hamilton (40.4%) | 40.35% | 201.75 | 403.5 | Discharge at SP ≥ $300-500/MWh (MCC $202+ at primary node) | Monitor trend; discharge on confirmed ramp
BCESW-SNDSW 345KV | 🟢 Active | HE17, HE18, HE16 | Not much activity here during summer and winter. Also see this one when south wind is sub 1GW. Consistent factor also seems to be days of strong south load (15GW+) during the solar window | Holcomb (11.0%) | 11% | 55 | 110 | Discharge at SP ≥ $500-800/MWh (MCC $55+ at node) | Monitor trend; discharge on confirmed ramp
LNGSW-CONSW 345KV | 🟢 Active | HE1, HE2, HE24 | Pretty well associated with high west wind gen. Prob 10GW+. Never really get shadow pricing above $400 here but we still have 20%sf at west sites. Also couples well with West RT load being over 9GW overnight | Judkins (21.3%) | 21.3% | 106.5 | 213 | Discharge at SP ≥ $300-500/MWh (MCC $106+ at primary node) | Monitor trend; discharge on confirmed ramp
YELWJCKT-FORTMA 138KV | 🟢 Active | HE7, HE6, HE5 | Very high west winds. See it the most at 13GW+ of west wind gen in offpeak hours and 10+GW of west wind gen in on-peak hours | — |  |  |  | Check MCC Calculator | Monitor trend; discharge on confirmed ramp
Legend: | 🟢 Active = detailed MCC analysis completed |  |  | — |  |  |  | Check MCC Calculator | Monitor trend; discharge on confirmed ramp
🟡 WATCH LINES — Monitor Closely in Jun – Aug
ASHERTON-CATARINA 138KV | 🟡 Watch | HE13, HE12, HE14 | All conesiton seen in solar window. Driven by super low coastal and south wind gen during the solar window. Maybe look into this more, doesn't seem load driven | Catarina (77.0%) | 76.98% | 384.91 | 769.82 | Discharge at SP ≥ $300-500/MWh (MCC $385+ at primary node) | Discharge on sight
MRVLY-ESTLD 69KV | 🟡 Watch | HE20, HE19, HE21 | Also seems to be when we see north load reach above 15GW. Especially if it's the load leader by a big chunk on the grid. Look at 01/11 and 01/12 | Cisco (17.3%) | 17.35% | 86.74 | 173.48 | Discharge at SP ≥ $500-800/MWh (MCC $87+ at node) | Discharge on sight
STP-WAP 345KV | 🟡 Watch | HE17, HE16, HE13 | Def has to do with houston load during the summer heat. When houston load reaches above 18GW+ we will see this flare up. | Mainland (9.6%) | 9.57% | 47.85 | 95.7 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight
PALOUSE-WOLFCAMP 138KV | 🟡 Watch | HE18, HE17, HE16 | Strongest pricing seen in the summer (hot). When RT West load gets up to 9GW we will see this, especially when solar is ramping offline. | Russek (30.6%) | 30.57% | 152.845 | 305.69 | Discharge at SP ≥ $300-500/MWh (MCC $153+ at primary node) | Discharge on sight
LPLMK-LPLNE 115KV | 🟡 Watch | HE21, HE22, HE20 | Don't have very strong shift factors out here in the west but active pretty often when west wind levels go below 5GW but it's actually strong panhandle winds that is the cause. | Judkins (1.6%) | 1.594% | 7.97 | 15.94 | Only strong pricing (SP>$2000) creates meaningful MCC | Discharge on sight
CRDSW-OLNEY 69KV | 🟡 Watch | HE17, HE18, HE16 | See this on hot days where North load reaches up to 22GW+. | Olney (78.7%) | 78.68% | 393.41 | 786.82 | Discharge at SP ≥ $300-500/MWh (MCC $393+ at primary node) | Discharge on sight
HONDOCK-DEVINESW 69KV | 🟡 Watch | HE16, HE18, HE17 | Newer constraint that showed up in January. Was strongest in march and april. Skip this one too weak of shift factor | — |  |  |  | Check MCC Calculator | Discharge on sight
I_FW_N | 🟡 Watch | HE5, HE6, HE4 | Never really see enough shadow pricing to create strong MCC's here. I also don't see one single issue | Judkins (15.7%) | 15.66% | 78.3 | 156.6 | Discharge at SP ≥ $500-800/MWh (MCC $78+ at node) | Discharge on sight
CARVER-TINSLEY 138KV | 🟡 Watch | HE21, HE20, HE22 | Most shadow pricing seen in HE11 and 12. See this with West wind at 10GW+ coupled with sub 2GW coastal winds | Hamilton (32.3%) | 32.32% | 161.615 | 323.23 | Discharge at SP ≥ $300-500/MWh (MCC $162+ at primary node) | Discharge on sight
BIG_FOOT-PLEASANT 138KV | 🟡 Watch | HE16, HE13, HE15 | Not that much action since RTC switchover. Too small of shift factors here… | — |  |  |  | Check MCC Calculator | Discharge on sight
MADDUX-TREADWEL 138KV | 🟡 Watch | HE17, HE18, HE16 | Haven't seen much post RTC+B should be interesting to look out for. Can't find much of a driver here. | Junction (39.3%) | 39.25% | 196.26 | 392.52 | Discharge at SP ≥ $300-500/MWh (MCC $196+ at primary node) | Discharge on sight
MAXWELL-HAMILTON 138KV | 🟡 Watch | HE2, HE24, HE1 | Will be interesting to see if this still plays in Post RTC + B. Associated with 13+GW of west wind generation. | Hamilton (23.0%) | 22.98% | 114.885 | 229.77 | Discharge at SP ≥ $300-500/MWh (MCC $115+ at primary node) | Discharge on sight
LNGSW-CONSW 345KV | 🟡 Watch | HE1, HE2, HE24 | Haven't seen this one since october 2025. May just be summer congestion. Associated with 10GW+ of west wind gen | Judkins (21.5%) | 21.3% | 106.5 | 213 | Discharge at SP ≥ $300-500/MWh (MCC $106+ at primary node) | Discharge on sight
SONR-ATSO 69KV | 🟡 Watch | HE1, HE3, HE2 | Don't really know what the driver is here. It could be west load surpassing 9GW+ overnight but not sure how common that is. The west wind levels are not very reliable but could be attributed with Low west winds OR high west winds | Russek (5.0%) | 5% | 25 | 50 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight
BRUNI 138KV | 🟡 Watch | HE23, HE22, HE21 | Our shift factors are only like 1% so can't really include this one. Maybe associated with 1.5GW+ of south wind gen | Catarina (1.0%) | 1.044% | 5.22 | 10.44 | Only strong pricing (SP>$2000) creates meaningful MCC | Discharge on sight
CRTRVLLE-HILGR 138KV | 🟡 Watch | HE1, HE2, HE23 | Never rlly seen MCC's over $50 for our west sites so not much to report on here. Driver here is 10GW+ of west wind gen | Judkins (4.0%) | 4% | 20 | 40 | Only strong pricing (SP>$2000) creates meaningful MCC | Discharge on sight
LA_PALMA-HAINE_DR 138KV | 🟡 Watch | HE17, HE16, HE18 | See this congestion with 2GW+ of south wind Gen and 2.5GW+ of coastal wind gen | Val Verde (1.9%) | 1.856% | 9.278 | 18.556 | Only strong pricing (SP>$2000) creates meaningful MCC | Discharge on sight
PILONCIL-NLARSW 138KV | 🟡 Watch | HE16, HE15, HE17 | see this with really low coastal and south winds. Like sub 1GW for each. | Holcomb (23.8%) | 23.81% | 119.035 | 238.07 | Discharge at SP ≥ $300-500/MWh (MCC $119+ at primary node) | Discharge on sight
MCCAMY | 🟡 Watch | HE13, HE12, HE14 | Delete, don’t see any shadow pricing | — |  |  |  | Check MCC Calculator | Discharge on sight
CMNSW-CMNTP 138KV | 🟡 Watch | HE17, HE19, HE18 | Get this congestion when coastal winds surpass 2.7GW+ of coastal gen. When system wide wind gen reaches to 20GW+ is where we get the best shadow pricing. Don't get much pricing from here though with low shift factors | Cisco (5.0%) | 5% | 25 | 50 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight
UVALDE-READING 138KV | 🟡 Watch | HE19, HE18, HE17 | Haven't seen post RTC. No good positive shift factor but hamilton has strong negative. Can't find a specific driver but 19GW+ of south load could be a driver with low south wind | — |  |  |  | Check MCC Calculator | Discharge on sight
WOLFCAMP-SANTARIT 138KV | 🟡 Watch | HE17, HE16, HE19 | No specific driver I can find here. Russek has a 32% shift factor here. High temps also tend to flair up this line. Only saw for 2 days in April | Russek (31.7%) | 31.74% | 158.695 | 317.39 | Discharge at SP ≥ $300-500/MWh (MCC $159+ at primary node) | Discharge on sight
LHSES-PRCSW 138KV | 🟡 Watch | HE20, HE19, HE17 | Skip this one. Only -5% shift factor here at North sites | — |  |  |  | Check MCC Calculator | Discharge on sight
LAREDO-DEL_MAR 138KV | 🟡 Watch | HE23, HE24, HE22 | Will be interesting to see if we see this congestion this summer. Not very strong pricing here though. Skip | Holcomb (6.0%) | 6% | 30 | 60 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight
FMRVL-RYSSW 345KV | 🟡 Watch | HE17, HE16, HE15 | Dibol only has a 6% shift factor here but seen shadow pricing in the thousands. Only saw decent shadow pricing for one day. Delete | Diboll (5.2%) | 5.227% | 26.135 | 52.27 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight

## 🍂 Fall
FALL CONGESTION PLAYBOOK ¦ Sep – Nov
Shoulder season. West wind ramps up. Watch overnight west wind gen.
Line / Constraint | Priority | Peak HE (Best Hours) | Driver / Trigger | Primary Node | SF (%) | MCC @ $500 SP | MCC @ $1000 SP | Discharge Guidance | Hold Strategy? | Key Gen Level Threshold | Operator Notes
🟢 ACTIVE LINES — Priority Targets for Sep – Nov
FORTMA-YELWJCKT 138KV | 🟢 Active | HE21, HE20, HE23 | Mostly seen overnight. Correlated when west dips below coastal wind generation. West wind gen generally has to be below 3GW | Junction (50.0%) | 50% | 250 | 500 | Discharge at SP ≥ $300-500/MWh (MCC $250+ at primary node) | Monitor trend; discharge on confirmed ramp
STP-ELMCREEK 345KV | 🟢 Active | HE22, HE21, HE23 | Mostly correlated with low renewable generation on the grid. See the congestion overnight with low (sub 8gw) of wind gen on the grid | Catarina (8.0%) | 8% | 40 | 80 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Monitor trend; discharge on confirmed ramp
WESTEX | 🟢 Active | HE20, HE19, HE12 | See flare up in days of high renewable generation. Seen in all hours of the day but most common during solar ramps or when west Gen reaches above 15GW overnight. | Diboll (19.4%) | 19.4% | 96.98 | 193.96 | Discharge at SP ≥ $500-800/MWh (MCC $97+ at node) | Monitor trend; discharge on confirmed ramp
LNGSW-PRLSW 345KV | 🟢 Active | HE1, HE2, HE24 | This congestion is seem mostly overnight. Main driver on this line is when we see west wind gen reach above 10GW. | Judkins (21.3%) | 21.33% | 106.645 | 213.29 | Discharge at SP ≥ $300-500/MWh (MCC $107+ at primary node) | Monitor trend; discharge on confirmed ramp
E_PASP | 🟢 Active | HE20, HE19, HE18 | This sends Val Verde negative. Strongest during down ramps best theory for congestion here is when south load reaches 18GW+. | Junction (4.0%) | 4% | 20 | 40 | Only strong pricing (SP>$2000) creates meaningful MCC | Monitor trend; discharge on confirmed ramp
NLARSW-PILONCIL 138KV | 🟢 Active | HE24, HE1, HE2 | This is a newer congestion… started in Nov 2025. see this congestion with coastal wind gen at 2.5GW+. Same with south wind | Catarina (26.0%) | 26% | 130 | 260 | Discharge at SP ≥ $300-500/MWh (MCC $130+ at primary node) | Monitor trend; discharge on confirmed ramp
MGSES-CATSW 345KV | 🟢 Active | HE23, HE19, HE20 | Newer congestion (start Nov 2025). Mostly see this congestion with cooler weather in the west creating higher load levels (9gw+) and wind sub 8GW. This ould be the inbalance of demand and wind gen. look into that also maybe coastal wind gen | Judkins (30.0%) | 30% | 150 | 300 | Discharge at SP ≥ $300-500/MWh (MCC $150+ at primary node) | Monitor trend; discharge on confirmed ramp
ESCONDID-GANSO 138KV | 🟢 Active | HE8, HE9, HE1 | HE 10 saw the most shadow pricing but morning all around get best pricing. We see this congestion with low wind generation online, especially the west goin sub 3GW paired with WTX seeing a 9GW+ load | Hamilton (40.4%) | 40.35% | 201.75 | 403.5 | Discharge at SP ≥ $300-500/MWh (MCC $202+ at primary node) | Monitor trend; discharge on confirmed ramp
BCESW-SNDSW 345KV | 🟢 Active | HE17, HE18, HE16 | Not much activity here during summer and winter. Also see this one when south wind is sub 1GW. Consistent factor also seems to be days of strong south load (15GW+) during the solar window | Holcomb (11.0%) | 11% | 55 | 110 | Discharge at SP ≥ $500-800/MWh (MCC $55+ at node) | Monitor trend; discharge on confirmed ramp
Legend: | 🟢 Active = detailed MCC analysis completed |  |  | — |  |  |  | Check MCC Calculator | Monitor trend; discharge on confirmed ramp
🟡 WATCH LINES — Monitor Closely in Sep – Nov
MRVLY-ESTLD 69KV | 🟡 Watch | HE20, HE19, HE21 | Also seems to be when we see north load reach above 15GW. Especially if it's the load leader by a big chunk on the grid. Look at 01/11 and 01/12 | Cisco (17.3%) | 17.35% | 86.74 | 173.48 | Discharge at SP ≥ $500-800/MWh (MCC $87+ at node) | Discharge on sight
PALOUSE-WOLFCAMP 138KV | 🟡 Watch | HE18, HE17, HE16 | Strongest pricing seen in the summer (hot). When RT West load gets up to 9GW we will see this, especially when solar is ramping offline. | Russek (30.6%) | 30.57% | 152.845 | 305.69 | Discharge at SP ≥ $300-500/MWh (MCC $153+ at primary node) | Discharge on sight
LPLMK-LPLNE 115KV | 🟡 Watch | HE21, HE22, HE20 | Don't have very strong shift factors out here in the west but active pretty often when west wind levels go below 5GW but it's actually strong panhandle winds that is the cause. | Judkins (1.6%) | 1.594% | 7.97 | 15.94 | Only strong pricing (SP>$2000) creates meaningful MCC | Discharge on sight
HONDOCK-DEVINESW 69KV | 🟡 Watch | HE16, HE18, HE17 | Newer constraint that showed up in January. Was strongest in march and april. Skip this one too weak of shift factor | — |  |  |  | Check MCC Calculator | Discharge on sight
I_FW_N | 🟡 Watch | HE5, HE6, HE4 | Never really see enough shadow pricing to create strong MCC's here. I also don't see one single issue | Judkins (15.7%) | 15.66% | 78.3 | 156.6 | Discharge at SP ≥ $500-800/MWh (MCC $78+ at node) | Discharge on sight
CARVER-TINSLEY 138KV | 🟡 Watch | HE21, HE20, HE22 | Most shadow pricing seen in HE11 and 12. See this with West wind at 10GW+ coupled with sub 2GW coastal winds | Hamilton (32.3%) | 32.32% | 161.615 | 323.23 | Discharge at SP ≥ $300-500/MWh (MCC $162+ at primary node) | Discharge on sight
MADDUX-TREADWEL 138KV | 🟡 Watch | HE17, HE18, HE16 | Haven't seen much post RTC+B should be interesting to look out for. Can't find much of a driver here. | Junction (39.3%) | 39.25% | 196.26 | 392.52 | Discharge at SP ≥ $300-500/MWh (MCC $196+ at primary node) | Discharge on sight
MAXWELL-HAMILTON 138KV | 🟡 Watch | HE2, HE24, HE1 | Will be interesting to see if this still plays in Post RTC + B. Associated with 13+GW of west wind generation. | Hamilton (23.0%) | 22.98% | 114.885 | 229.77 | Discharge at SP ≥ $300-500/MWh (MCC $115+ at primary node) | Discharge on sight
SONR-ATSO 69KV | 🟡 Watch | HE1, HE3, HE2 | Don't really know what the driver is here. It could be west load surpassing 9GW+ overnight but not sure how common that is. The west wind levels are not very reliable but could be attributed with Low west winds OR high west winds | Russek (5.0%) | 5% | 25 | 50 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight
BRUNI 138KV | 🟡 Watch | HE23, HE22, HE21 | Our shift factors are only like 1% so can't really include this one. Maybe associated with 1.5GW+ of south wind gen | Catarina (1.0%) | 1.044% | 5.22 | 10.44 | Only strong pricing (SP>$2000) creates meaningful MCC | Discharge on sight
CRTRVLLE-HILGR 138KV | 🟡 Watch | HE1, HE2, HE23 | Never rlly seen MCC's over $50 for our west sites so not much to report on here. Driver here is 10GW+ of west wind gen | Judkins (4.0%) | 4% | 20 | 40 | Only strong pricing (SP>$2000) creates meaningful MCC | Discharge on sight
PILONCIL-NLARSW 138KV | 🟡 Watch | HE16, HE15, HE17 | see this with really low coastal and south winds. Like sub 1GW for each. | Holcomb (23.8%) | 23.81% | 119.035 | 238.07 | Discharge at SP ≥ $300-500/MWh (MCC $119+ at primary node) | Discharge on sight
MCCAMY | 🟡 Watch | HE13, HE12, HE14 | Delete, don’t see any shadow pricing | — |  |  |  | Check MCC Calculator | Discharge on sight
CMNSW-CMNTP 138KV | 🟡 Watch | HE17, HE19, HE18 | Get this congestion when coastal winds surpass 2.7GW+ of coastal gen. When system wide wind gen reaches to 20GW+ is where we get the best shadow pricing. Don't get much pricing from here though with low shift factors | Cisco (5.0%) | 5% | 25 | 50 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight
WOLFCAMP-SANTARIT 138KV | 🟡 Watch | HE17, HE16, HE19 | No specific driver I can find here. Russek has a 32% shift factor here. High temps also tend to flair up this line. Only saw for 2 days in April | Russek (31.7%) | 31.74% | 158.695 | 317.39 | Discharge at SP ≥ $300-500/MWh (MCC $159+ at primary node) | Discharge on sight
LHSES-PRCSW 138KV | 🟡 Watch | HE20, HE19, HE17 | Skip this one. Only -5% shift factor here at North sites | — |  |  |  | Check MCC Calculator | Discharge on sight
FMRVL-RYSSW 345KV | 🟡 Watch | HE17, HE16, HE15 | Dibol only has a 6% shift factor here but seen shadow pricing in the thousands. Only saw decent shadow pricing for one day. Delete | Diboll (5.2%) | 5.227% | 26.135 | 52.27 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight

## ❄️ Winter
WINTER CONGESTION PLAYBOOK ¦ Dec – Feb
Cold load events. Low renewables overnight. STP-ELMCREEK very active.
Line / Constraint | Priority | Peak HE (Best Hours) | Driver / Trigger | Primary Node | SF (%) | MCC @ $500 SP | MCC @ $1000 SP | Discharge Guidance | Hold Strategy? | Key Gen Level Threshold | Operator Notes
🟢 ACTIVE LINES — Priority Targets for Dec – Feb
TWINBU-HARGROVE 138KV | 🟢 Active | HE5, HE6, HE4 | West wind sub 5GW is when we see it strongest. Possible to see around sub 8Gw | Russek (31.7%) | 31.66% | 158.325 | 316.65 | Discharge at SP ≥ $300-500/MWh (MCC $158+ at primary node) | Yes — hold for higher pricing overnight |  | Willing to sit on high pricing HE20-24.
FORTMA-YELWJCKT 138KV | 🟢 Active | HE21, HE20, HE23 | Mostly seen overnight. Correlated when west dips below coastal wind generation. West wind gen generally has to be below 3GW | Junction (50.0%) | 50% | 250 | 500 | Discharge at SP ≥ $300-500/MWh (MCC $250+ at primary node) | Monitor trend; discharge on confirmed ramp
STP-ELMCREEK 345KV | 🟢 Active | HE22, HE21, HE23 | Mostly correlated with low renewable generation on the grid. See the congestion overnight with low (sub 8gw) of wind gen on the grid | Catarina (8.0%) | 8% | 40 | 80 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Monitor trend; discharge on confirmed ramp
LASCRUCE-MILO 138KV | 🟢 Active | HE20, HE19, HE21 | south AND coastal wind gen at 2GW+ | Holcomb (28.0%) | 28.02% | 140.125 | 280.25 | Discharge at SP ≥ $300-500/MWh (MCC $140+ at primary node) | Monitor trend; discharge on confirmed ramp
WESTEX | 🟢 Active | HE20, HE19, HE12 | See flare up in days of high renewable generation. Seen in all hours of the day but most common during solar ramps or when west Gen reaches above 15GW overnight. | Diboll (19.4%) | 19.4% | 96.98 | 193.96 | Discharge at SP ≥ $500-800/MWh (MCC $97+ at node) | Monitor trend; discharge on confirmed ramp
LNGSW-PRLSW 345KV | 🟢 Active | HE1, HE2, HE24 | This congestion is seem mostly overnight. Main driver on this line is when we see west wind gen reach above 10GW. | Judkins (21.3%) | 21.33% | 106.645 | 213.29 | Discharge at SP ≥ $300-500/MWh (MCC $107+ at primary node) | Monitor trend; discharge on confirmed ramp
E_PASP | 🟢 Active | HE20, HE19, HE18 | This sends Val Verde negative. Strongest during down ramps best theory for congestion here is when south load reaches 18GW+. | Junction (4.0%) | 4% | 20 | 40 | Only strong pricing (SP>$2000) creates meaningful MCC | Monitor trend; discharge on confirmed ramp
NLARSW-PILONCIL 138KV | 🟢 Active | HE24, HE1, HE2 | This is a newer congestion… started in Nov 2025. see this congestion with coastal wind gen at 2.5GW+. Same with south wind | Catarina (26.0%) | 26% | 130 | 260 | Discharge at SP ≥ $300-500/MWh (MCC $130+ at primary node) | Monitor trend; discharge on confirmed ramp
MGSES-CATSW 345KV | 🟢 Active | HE23, HE19, HE20 | Newer congestion (start Nov 2025). Mostly see this congestion with cooler weather in the west creating higher load levels (9gw+) and wind sub 8GW. This ould be the inbalance of demand and wind gen. look into that also maybe coastal wind gen | Judkins (30.0%) | 30% | 150 | 300 | Discharge at SP ≥ $300-500/MWh (MCC $150+ at primary node) | Monitor trend; discharge on confirmed ramp
LOBO-LARDVNTH 138KV | 🟢 Active | HE22, HE19, HE21 | Newer Congestion (First seen Feb 2026). Can be seen at all times throughout the day but mostly 17-3. Correlates with 2.5GW+ of south wind or 2.8GW+ of coastal wind. Maybe was also outage driven bc we haven't seen it since march. | Holcomb (32.4%) | 32.39% | 161.93 | 323.86 | Discharge at SP ≥ $300-500/MWh (MCC $162+ at primary node) | Monitor trend; discharge on confirmed ramp
ESCONDID-GANSO 138KV | 🟢 Active | HE8, HE9, HE1 | HE 10 saw the most shadow pricing but morning all around get best pricing. We see this congestion with low wind generation online, especially the west goin sub 3GW paired with WTX seeing a 9GW+ load | Hamilton (40.4%) | 40.35% | 201.75 | 403.5 | Discharge at SP ≥ $300-500/MWh (MCC $202+ at primary node) | Monitor trend; discharge on confirmed ramp
BCESW-SNDSW 345KV | 🟢 Active | HE17, HE18, HE16 | Not much activity here during summer and winter. Also see this one when south wind is sub 1GW. Consistent factor also seems to be days of strong south load (15GW+) during the solar window | Holcomb (11.0%) | 11% | 55 | 110 | Discharge at SP ≥ $500-800/MWh (MCC $55+ at node) | Monitor trend; discharge on confirmed ramp
Legend: | 🟢 Active = detailed MCC analysis completed |  |  | — |  |  |  | Check MCC Calculator | Monitor trend; discharge on confirmed ramp
🟡 WATCH LINES — Monitor Closely in Dec – Feb
MRVLY-ESTLD 69KV | 🟡 Watch | HE20, HE19, HE21 | Also seems to be when we see north load reach above 15GW. Especially if it's the load leader by a big chunk on the grid. Look at 01/11 and 01/12 | Cisco (17.3%) | 17.35% | 86.74 | 173.48 | Discharge at SP ≥ $500-800/MWh (MCC $87+ at node) | Discharge on sight
PALOUSE-WOLFCAMP 138KV | 🟡 Watch | HE18, HE17, HE16 | Strongest pricing seen in the summer (hot). When RT West load gets up to 9GW we will see this, especially when solar is ramping offline. | Russek (30.6%) | 30.57% | 152.845 | 305.69 | Discharge at SP ≥ $300-500/MWh (MCC $153+ at primary node) | Discharge on sight
LPLMK-LPLNE 115KV | 🟡 Watch | HE21, HE22, HE20 | Don't have very strong shift factors out here in the west but active pretty often when west wind levels go below 5GW but it's actually strong panhandle winds that is the cause. | Judkins (1.6%) | 1.594% | 7.97 | 15.94 | Only strong pricing (SP>$2000) creates meaningful MCC | Discharge on sight
HONDOCK-DEVINESW 69KV | 🟡 Watch | HE16, HE18, HE17 | Newer constraint that showed up in January. Was strongest in march and april. Skip this one too weak of shift factor | — |  |  |  | Check MCC Calculator | Discharge on sight
I_FW_N | 🟡 Watch | HE5, HE6, HE4 | Never really see enough shadow pricing to create strong MCC's here. I also don't see one single issue | Judkins (15.7%) | 15.66% | 78.3 | 156.6 | Discharge at SP ≥ $500-800/MWh (MCC $78+ at node) | Discharge on sight
CARVER-TINSLEY 138KV | 🟡 Watch | HE21, HE20, HE22 | Most shadow pricing seen in HE11 and 12. See this with West wind at 10GW+ coupled with sub 2GW coastal winds | Hamilton (32.3%) | 32.32% | 161.615 | 323.23 | Discharge at SP ≥ $300-500/MWh (MCC $162+ at primary node) | Discharge on sight
MASN-KATEMCY 69KV | 🟡 Watch | HE19, HE18, HE23 | Affiliated with low west wind and low north wind gen | Junction (25.1%) | 25.1% | 125.5 | 251 | Discharge at SP ≥ $300-500/MWh (MCC $126+ at primary node) | Discharge on sight
SAMSW-VENSW 345KV | 🟡 Watch | HE11, HE12, HE13 | This was strongest in December and Jan, seen in May too. Think its around all seasons. Really no idea what the cause is, look into more, | Diboll (5.3%) | 5.3% | 26.5 | 53 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight
MADDUX-TREADWEL 138KV | 🟡 Watch | HE17, HE18, HE16 | Haven't seen much post RTC+B should be interesting to look out for. Can't find much of a driver here. | Junction (39.3%) | 39.25% | 196.26 | 392.52 | Discharge at SP ≥ $300-500/MWh (MCC $196+ at primary node) | Discharge on sight
PRLSW-CONSW 345KV | 🟡 Watch | HE2, HE4, HE1 | Believe we see this congestion with more mild temps, lower loads, and over 8GW+ of west wind generation | Judkins (29.0%) | 29.04% | 145.215 | 290.43 | Discharge at SP ≥ $300-500/MWh (MCC $145+ at primary node) | Discharge on sight
MAXWELL-HAMILTON 138KV | 🟡 Watch | HE2, HE24, HE1 | Will be interesting to see if this still plays in Post RTC + B. Associated with 13+GW of west wind generation. | Hamilton (23.0%) | 22.98% | 114.885 | 229.77 | Discharge at SP ≥ $300-500/MWh (MCC $115+ at primary node) | Discharge on sight
SONR-ATSO 69KV | 🟡 Watch | HE1, HE3, HE2 | Don't really know what the driver is here. It could be west load surpassing 9GW+ overnight but not sure how common that is. The west wind levels are not very reliable but could be attributed with Low west winds OR high west winds | Russek (5.0%) | 5% | 25 | 50 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight
BRUNI 138KV | 🟡 Watch | HE23, HE22, HE21 | Our shift factors are only like 1% so can't really include this one. Maybe associated with 1.5GW+ of south wind gen | Catarina (1.0%) | 1.044% | 5.22 | 10.44 | Only strong pricing (SP>$2000) creates meaningful MCC | Discharge on sight
CRTRVLLE-HILGR 138KV | 🟡 Watch | HE1, HE2, HE23 | Never rlly seen MCC's over $50 for our west sites so not much to report on here. Driver here is 10GW+ of west wind gen | Judkins (4.0%) | 4% | 20 | 40 | Only strong pricing (SP>$2000) creates meaningful MCC | Discharge on sight
ARGYL-LWSVH 138KV | 🟡 Watch | HE1, HE2, HE24 | Mostly seen in all hour during the winter season. See it when wind patterns reach above 12GW. I would look into this one some more. | Diboll (1.5%) | 1.469% | 7.345 | 14.69 | Only strong pricing (SP>$2000) creates meaningful MCC | Discharge on sight
PILONCIL-NLARSW 138KV | 🟡 Watch | HE16, HE15, HE17 | see this with really low coastal and south winds. Like sub 1GW for each. | Holcomb (23.8%) | 23.81% | 119.035 | 238.07 | Discharge at SP ≥ $300-500/MWh (MCC $119+ at primary node) | Discharge on sight
MCCAMY | 🟡 Watch | HE13, HE12, HE14 | Delete, don’t see any shadow pricing | — |  |  |  | Check MCC Calculator | Discharge on sight
CMNSW-CMNTP 138KV | 🟡 Watch | HE17, HE19, HE18 | Get this congestion when coastal winds surpass 2.7GW+ of coastal gen. When system wide wind gen reaches to 20GW+ is where we get the best shadow pricing. Don't get much pricing from here though with low shift factors | Cisco (5.0%) | 5% | 25 | 50 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight
WOLFCAMP-SANTARIT 138KV | 🟡 Watch | HE17, HE16, HE19 | No specific driver I can find here. Russek has a 32% shift factor here. High temps also tend to flair up this line. Only saw for 2 days in April | Russek (31.7%) | 31.74% | 158.695 | 317.39 | Discharge at SP ≥ $300-500/MWh (MCC $159+ at primary node) | Discharge on sight
LHSES-PRCSW 138KV | 🟡 Watch | HE20, HE19, HE17 | Skip this one. Only -5% shift factor here at North sites | — |  |  |  | Check MCC Calculator | Discharge on sight
FMRVL-RYSSW 345KV | 🟡 Watch | HE17, HE16, HE15 | Dibol only has a 6% shift factor here but seen shadow pricing in the thousands. Only saw decent shadow pricing for one day. Delete | Diboll (5.2%) | 5.227% | 26.135 | 52.27 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight

## 🌱 Spring
SPRING CONGESTION PLAYBOOK ¦ Mar – May
Shoulder season. High system-wide wind events. Coastal & south wind ramps.
Line / Constraint | Priority | Peak HE (Best Hours) | Driver / Trigger | Primary Node | SF (%) | MCC @ $500 SP | MCC @ $1000 SP | Discharge Guidance | Hold Strategy? | Key Gen Level Threshold | Operator Notes
🟢 ACTIVE LINES — Priority Targets for Mar – May
FORTMA-YELWJCKT 138KV | 🟢 Active | HE21, HE20, HE23 | Mostly seen overnight. Correlated when west dips below coastal wind generation. West wind gen generally has to be below 3GW | Junction (50.0%) | 50% | 250 | 500 | Discharge at SP ≥ $300-500/MWh (MCC $250+ at primary node) | Monitor trend; discharge on confirmed ramp
WESTEX | 🟢 Active | HE20, HE19, HE12 | See flare up in days of high renewable generation. Seen in all hours of the day but most common during solar ramps or when west Gen reaches above 15GW overnight. | Diboll (19.4%) | 19.4% | 96.98 | 193.96 | Discharge at SP ≥ $500-800/MWh (MCC $97+ at node) | Monitor trend; discharge on confirmed ramp
LNGSW-PRLSW 345KV | 🟢 Active | HE1, HE2, HE24 | This congestion is seem mostly overnight. Main driver on this line is when we see west wind gen reach above 10GW. | Judkins (21.3%) | 21.33% | 106.645 | 213.29 | Discharge at SP ≥ $300-500/MWh (MCC $107+ at primary node) | Monitor trend; discharge on confirmed ramp
E_PASP | 🟢 Active | HE20, HE19, HE18 | This sends Val Verde negative. Strongest during down ramps best theory for congestion here is when south load reaches 18GW+. | Junction (4.0%) | 4% | 20 | 40 | Only strong pricing (SP>$2000) creates meaningful MCC | Monitor trend; discharge on confirmed ramp
NLARSW-PILONCIL 138KV | 🟢 Active | HE24, HE1, HE2 | This is a newer congestion… started in Nov 2025. see this congestion with coastal wind gen at 2.5GW+. Same with south wind | Catarina (26.0%) | 26% | 130 | 260 | Discharge at SP ≥ $300-500/MWh (MCC $130+ at primary node) | Monitor trend; discharge on confirmed ramp
MGSES-CATSW 345KV | 🟢 Active | HE23, HE19, HE20 | Newer congestion (start Nov 2025). Mostly see this congestion with cooler weather in the west creating higher load levels (9gw+) and wind sub 8GW. This ould be the inbalance of demand and wind gen. look into that also maybe coastal wind gen | Judkins (30.0%) | 30% | 150 | 300 | Discharge at SP ≥ $300-500/MWh (MCC $150+ at primary node) | Monitor trend; discharge on confirmed ramp
LOBO-LARDVNTH 138KV | 🟢 Active | HE22, HE19, HE21 | Newer Congestion (First seen Feb 2026). Can be seen at all times throughout the day but mostly 17-3. Correlates with 2.5GW+ of south wind or 2.8GW+ of coastal wind. Maybe was also outage driven bc we haven't seen it since march. | Holcomb (32.4%) | 32.39% | 161.93 | 323.86 | Discharge at SP ≥ $300-500/MWh (MCC $162+ at primary node) | Monitor trend; discharge on confirmed ramp
ESCONDID-GANSO 138KV | 🟢 Active | HE8, HE9, HE1 | HE 10 saw the most shadow pricing but morning all around get best pricing. We see this congestion with low wind generation online, especially the west goin sub 3GW paired with WTX seeing a 9GW+ load | Hamilton (40.4%) | 40.35% | 201.75 | 403.5 | Discharge at SP ≥ $300-500/MWh (MCC $202+ at primary node) | Monitor trend; discharge on confirmed ramp
BCESW-SNDSW 345KV | 🟢 Active | HE17, HE18, HE16 | Not much activity here during summer and winter. Also see this one when south wind is sub 1GW. Consistent factor also seems to be days of strong south load (15GW+) during the solar window | Holcomb (11.0%) | 11% | 55 | 110 | Discharge at SP ≥ $500-800/MWh (MCC $55+ at node) | Monitor trend; discharge on confirmed ramp
YELWJCKT-FORTMA 138KV | 🟢 Active | HE7, HE6, HE5 | Very high west winds. See it the most at 13GW+ of west wind gen in offpeak hours and 10+GW of west wind gen in on-peak hours | — |  |  |  | Check MCC Calculator | Monitor trend; discharge on confirmed ramp
Legend: | 🟢 Active = detailed MCC analysis completed |  |  | — |  |  |  | Check MCC Calculator | Monitor trend; discharge on confirmed ramp
🟡 WATCH LINES — Monitor Closely in Mar – May
MRVLY-ESTLD 69KV | 🟡 Watch | HE20, HE19, HE21 | Also seems to be when we see north load reach above 15GW. Especially if it's the load leader by a big chunk on the grid. Look at 01/11 and 01/12 | Cisco (17.3%) | 17.35% | 86.74 | 173.48 | Discharge at SP ≥ $500-800/MWh (MCC $87+ at node) | Discharge on sight
PALOUSE-WOLFCAMP 138KV | 🟡 Watch | HE18, HE17, HE16 | Strongest pricing seen in the summer (hot). When RT West load gets up to 9GW we will see this, especially when solar is ramping offline. | Russek (30.6%) | 30.57% | 152.845 | 305.69 | Discharge at SP ≥ $300-500/MWh (MCC $153+ at primary node) | Discharge on sight
LPLMK-LPLNE 115KV | 🟡 Watch | HE21, HE22, HE20 | Don't have very strong shift factors out here in the west but active pretty often when west wind levels go below 5GW but it's actually strong panhandle winds that is the cause. | Judkins (1.6%) | 1.594% | 7.97 | 15.94 | Only strong pricing (SP>$2000) creates meaningful MCC | Discharge on sight
CRDSW-OLNEY 69KV | 🟡 Watch | HE17, HE18, HE16 | See this on hot days where North load reaches up to 22GW+. | Olney (78.7%) | 78.68% | 393.41 | 786.82 | Discharge at SP ≥ $300-500/MWh (MCC $393+ at primary node) | Discharge on sight
HONDOCK-DEVINESW 69KV | 🟡 Watch | HE16, HE18, HE17 | Newer constraint that showed up in January. Was strongest in march and april. Skip this one too weak of shift factor | — |  |  |  | Check MCC Calculator | Discharge on sight
I_FW_N | 🟡 Watch | HE5, HE6, HE4 | Never really see enough shadow pricing to create strong MCC's here. I also don't see one single issue | Judkins (15.7%) | 15.66% | 78.3 | 156.6 | Discharge at SP ≥ $500-800/MWh (MCC $78+ at node) | Discharge on sight
CARVER-TINSLEY 138KV | 🟡 Watch | HE21, HE20, HE22 | Most shadow pricing seen in HE11 and 12. See this with West wind at 10GW+ coupled with sub 2GW coastal winds | Hamilton (32.3%) | 32.32% | 161.615 | 323.23 | Discharge at SP ≥ $300-500/MWh (MCC $162+ at primary node) | Discharge on sight
KLNSW-HHSTH 138KV | 🟡 Watch | HE22, HE23, HE2 | Newer congestion mostly seen in the spring. Esp march and april. Seen all hours but mostly during overnight period. We typically see this congestion when ERCOT wind gen reaches around 24GW+ | — |  |  |  | Check MCC Calculator | Discharge on sight
MADDUX-TREADWEL 138KV | 🟡 Watch | HE17, HE18, HE16 | Haven't seen much post RTC+B should be interesting to look out for. Can't find much of a driver here. | Junction (39.3%) | 39.25% | 196.26 | 392.52 | Discharge at SP ≥ $300-500/MWh (MCC $196+ at primary node) | Discharge on sight
PRLSW-CONSW 345KV | 🟡 Watch | HE2, HE4, HE1 | Believe we see this congestion with more mild temps, lower loads, and over 8GW+ of west wind generation | Judkins (29.0%) | 29.04% | 145.215 | 290.43 | Discharge at SP ≥ $300-500/MWh (MCC $145+ at primary node) | Discharge on sight
MAXWELL-HAMILTON 138KV | 🟡 Watch | HE2, HE24, HE1 | Will be interesting to see if this still plays in Post RTC + B. Associated with 13+GW of west wind generation. | Hamilton (23.0%) | 22.98% | 114.885 | 229.77 | Discharge at SP ≥ $300-500/MWh (MCC $115+ at primary node) | Discharge on sight
SONR-ATSO 69KV | 🟡 Watch | HE1, HE3, HE2 | Don't really know what the driver is here. It could be west load surpassing 9GW+ overnight but not sure how common that is. The west wind levels are not very reliable but could be attributed with Low west winds OR high west winds | Russek (5.0%) | 5% | 25 | 50 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight
LAKENASW-SAMATHIS 69KV | 🟡 Watch | HE1, HE4, HE24 | See this with low West wind Generation. More specifically sub 6GW of Gen | Russek (7.3%) | 7.252% | 36.26 | 72.52 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight
BRUNI 138KV | 🟡 Watch | HE23, HE22, HE21 | Our shift factors are only like 1% so can't really include this one. Maybe associated with 1.5GW+ of south wind gen | Catarina (1.0%) | 1.044% | 5.22 | 10.44 | Only strong pricing (SP>$2000) creates meaningful MCC | Discharge on sight
CRTRVLLE-HILGR 138KV | 🟡 Watch | HE1, HE2, HE23 | Never rlly seen MCC's over $50 for our west sites so not much to report on here. Driver here is 10GW+ of west wind gen | Judkins (4.0%) | 4% | 20 | 40 | Only strong pricing (SP>$2000) creates meaningful MCC | Discharge on sight
NORTMC-CROSSOVE 138KV | 🟡 Watch | HE19, HE17, HE16 | Above 9.5GW+ of west load. Mostly see it also when west temps reached above 91 degrees which is correlated with load patterns | Russek (34.2%) | 34.17% | 170.855 | 341.71 | Discharge at SP ≥ $300-500/MWh (MCC $171+ at primary node) | Discharge on sight
LA_PALMA-HAINE_DR 138KV | 🟡 Watch | HE17, HE16, HE18 | See this congestion with 2GW+ of south wind Gen and 2.5GW+ of coastal wind gen | Val Verde (1.9%) | 1.856% | 9.278 | 18.556 | Only strong pricing (SP>$2000) creates meaningful MCC | Discharge on sight
GN-PZ 138KV | 🟡 Watch | HE16, HE14, HE17 | High coastal wind generation, specifically around 2GW+ | Mainland (18.3%) | 18.32% | 91.61 | 183.22 | Discharge at SP ≥ $500-800/MWh (MCC $92+ at node) | Discharge on sight
PILONCIL-NLARSW 138KV | 🟡 Watch | HE16, HE15, HE17 | see this with really low coastal and south winds. Like sub 1GW for each. | Holcomb (23.8%) | 23.81% | 119.035 | 238.07 | Discharge at SP ≥ $300-500/MWh (MCC $119+ at primary node) | Discharge on sight
MV_BURNS-MV_HBRG4 138KV | 🟡 Watch | HE17, HE18, HE19 | Common to see when you get 3GW+ of coastal wind levels. Saw most shadow pricing in april of 2026. having 2+GW of south wind stacked also makes the line bind | Val Verde (15.3%) | 15.34% | 76.715 | 153.43 | Discharge at SP ≥ $500-800/MWh (MCC $77+ at node) | Discharge on sight
CATARINA-ASHERTON 138KV | 🟡 Watch | HE22, HE21, HE20 | Have not seen much shadow pricing from here in the past year. We get this congestion with 2.5GW of coastal wind and 2.1GW+ of south wind gen | Hamilton (7.2%) | 7.22% | 36.1 | 72.2 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight
BR-HOC 138KV | 🟡 Watch | HE16, HE15, HE17 | Common to see with 2.7GW+ of coastal wind gen and 2.5GW of south wind gen. can see in all hours of the day but most common in HE10-18. | Mainland (9.5%) | 9.515% | 47.575 | 95.15 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight
BOW 69KV | 🟡 Watch | HE9, HE8, HE20 | Pretty new congestion here. Seen march, april and may of 26. We see this congestion with high system-wide winds. Around like 20GW+ of wind gen | — |  |  |  | Check MCC Calculator | Discharge on sight
MCCAMY | 🟡 Watch | HE13, HE12, HE14 | Delete, don’t see any shadow pricing | — |  |  |  | Check MCC Calculator | Discharge on sight
CMNSW-CMNTP 138KV | 🟡 Watch | HE17, HE19, HE18 | Get this congestion when coastal winds surpass 2.7GW+ of coastal gen. When system wide wind gen reaches to 20GW+ is where we get the best shadow pricing. Don't get much pricing from here though with low shift factors | Cisco (5.0%) | 5% | 25 | 50 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight
WOLFCAMP-SANTARIT 138KV | 🟡 Watch | HE17, HE16, HE19 | No specific driver I can find here. Russek has a 32% shift factor here. High temps also tend to flair up this line. Only saw for 2 days in April | Russek (31.7%) | 31.74% | 158.695 | 317.39 | Discharge at SP ≥ $300-500/MWh (MCC $159+ at primary node) | Discharge on sight
LHSES-PRCSW 138KV | 🟡 Watch | HE20, HE19, HE17 | Skip this one. Only -5% shift factor here at North sites | — |  |  |  | Check MCC Calculator | Discharge on sight
COLETO CREEK-VICTORIA | 🟡 Watch | HE20, HE22, HE21 | Strong hours are HE20-1 but seen across all hours. This seems to be all coastal wind generated. When we get over 2.4GW of coastal wind gen, theres a good change we'll see this. Strongest shadow pricing has come from coastal wind at 3GW+ | — |  |  |  | Check MCC Calculator | Discharge on sight
FMRVL-RYSSW 345KV | 🟡 Watch | HE17, HE16, HE15 | Dibol only has a 6% shift factor here but seen shadow pricing in the thousands. Only saw decent shadow pricing for one day. Delete | Diboll (5.2%) | 5.227% | 26.135 | 52.27 | Discharge at SP ≥ $1000+/MWh (Need strong pricing for good MCC) | Discharge on sight

## 📊 Shift Factors
NODAL SHIFT FACTOR REFERENCE TABLE — Source: ERCOT Historical Study (Apr 2025 – May 2026)
Shift Factor = % of the line's shadow price passed through to that node as MCC. Blank = node not significantly exposed. Negative = inverse exposure.
Line / Constraint | Priority | Total Shadow $ | Peak HEs | Russek | Catarina | Holcomb | Hamilton | Fort Duncan | Junction | Judkins | Saddleback | Val Verde | Mainland | Cisco | Diboll | Olney | West TX Range (10 sites) | North TX Range (4 sites) | Coastal Range (5 sites) | Notable Non-Premium Site(s)
TWINBU-HARGROVE 138KV | 🟢 Active | 812338.3 | HE5, HE6, HE4 | 31.66% |  |  | 6.79% | 4.386% |  | 1.781% | 2.485% | [5 empty] | 0.0106 to 0.0350 | -0.0035 to -0.0033 | -0.0039 to -0.0026
LARDVNTH-LASCRUCE 138KV | 🟢 Active | 150133.74 | HE20, HE21, HE22 | 1% | 17.89% | 29.74% | 6.158% |  |  |  |  | -7.9% |  |  |  |  | 0.0062 to 0.0076 | 0.0035 to 0.0042 | -0.0971 to -0.0039 | Falfurrias (Coastal): -0.0971
FORTMA-YELWJCKT 138KV | 🟢 Active | 103773.93 | HE21, HE20, HE23 | 3.2% |  |  |  |  | 50% | 2% | 2% | [5 empty] | 0.0188 to 0.0199 | 0.0038 to 0.0074 | -0.0133 to -0.0087
STP-ELMCREEK 345KV | 🟢 Active | 89021.72 | HE22, HE21, HE23 | 4.2% | 8% | 7.9% | 6.7% | 7.5% | 5.8% | 3.7% | 3.9% | 5.2% | -9% | 2.3% |  | 2% | 0.0157 to 0.0215 | -0.0080 to 0.0011 | -0.0714 to 0.0561
TREADWEL-YELWJCKT 138KV | 🟢 Active | 99801.11 | HE17, HE18, HE19 |  | 1.5% | 1.5% |  |  | 46.76% |  |  | 1.5% |  |  |  |  | -0.0231 to -0.0025 | -0.0094 to -0.0050 | 0.0100 to 0.0146
LASCRUCE-MILO 138KV | 🟢 Active | 59751.88 | HE20, HE19, HE21 |  | 17.26% | 28.02% | 7% | 9.648% |  |  |  | -8% |  |  |  |  | 0.0060 to 0.0074 | 0.0037 to 0.0045 | -0.0970 to 0.0124 | Falfurrias (Coastal): -0.0970
WESTEX | 🟢 Active | 8701.73 | HE20, HE19, HE12 | -66% | 7.514% | 13.07% | -23% | -7% | -30% | -71.8% | -71.6% | 15.33% | 17.94% | -51.3% | 19.4% | -55.8% | -0.7100 | -0.0400 to 0.1970 | 0.1500 to 0.1700
LNGSW-PRLSW 345KV | 🟢 Active | 56393.44 | HE1, HE2, HE24 | 7% | -2% | -2% | 2% | 2% | -2% | 21.33% | 20.41% | -2% | -2% | -2% | -2% | -2% | 0.0196 to 0.2149 | -0.0464 to -0.0380 | -0.0130 to -0.0010
E_PASP | 🟢 Active | 84322.9 | HE20, HE19, HE18 |  | -8.556% | -13.78% |  |  | 4% |  |  | -19.62% |  |  |  |  | 0.0081 to 0.0134 | -0.0036 to 0.0006 | -0.2306 to -0.0771
NLARSW-PILONCIL 138KV | 🟢 Active | 59654.53 | HE24, HE1, HE2 |  | 26% | -9% | 8.633% | 12% |  |  |  | -6% |  |  |  |  | 0.0060 | 0.0030 to 0.0040 | -0.0591 to 0.0017 | Falfurrias (Coastal): -0.0591
MGSES-CATSW 345KV | 🟢 Active | 31442.57 | HE23, HE19, HE20 | 10% | [5 empty] | 30% | 27.04% |  | -5% | -8% | -6% | -7% | 0.1990 to 0.2420 | -0.0660 to -0.0550 | -0.0150 to 0.0008
LOBO-LARDVNTH 138KV | 🟢 Active | 37951.02 | HE22, HE19, HE21 |  | 21.82% | 32.39% | 7% | 7% |  |  |  | -7% |  |  |  |  | 0.0020 | 0.0001 to 0.0008 | -0.1030 to 0.0180 | Falfurrias (Coastal): -0.1030
ESCONDID-GANSO 138KV | 🟢 Active | 33325.75 | HE8, HE9, HE1 | 5% | -9.4% | -4.4% | 40.35% | -26.14% | [8 empty] | 0.0170 | 0.0020 to 0.0040 | -0.0190 to -0.0080
BCESW-SNDSW 345KV | 🟢 Active | 32240.3 | HE17, HE18, HE16 |  | 10% | 11% | 7% | 9% |  | -4% | -4% | 11% |  | -6% | -7.4% | -6.5% | -0.0480 to -0.0350 | -0.0780 to -0.0740 | 0.0600 to 0.1050
LNGSW-CONSW 345KV | 🟢 Active | 30989.79 | HE1, HE2, HE24 | 8% | [5 empty] | 21.3% | 20% | [5 empty] | 0.0800 to 0.2000 | -0.0220 to -0.0210 | -0.0220 to -0.0200
YELWJCKT-FORTMA 138KV | 🟢 Active | 18780.08 | HE7, HE6, HE5 | [5 empty] | -50% | [7 empty] | -0.0200 | — | 0.0150
Legend: | 🟢 Active = detailed MCC analysis completed | 0
ASHERTON-CATARINA 138KV | 🟡 Watch | 23033.53 | HE13, HE12, HE14 |  | 76.98% | 17.24% | -9% | -11.6% | [8 empty] | — | — | 0.0130
MRVLY-ESTLD 69KV | 🟡 Watch | 134306.39 | HE20, HE19, HE21 | [10 empty] | 17.35% |  |  | 0.0023 to 0.0026 | -0.0036 to -0.0016 | -0.0001 to 0.0004
STP-WAP 345KV | 🟡 Watch | 33834.4 | HE17, HE16, HE13 |  | -8.5% | -9.462% | -5% | -7% |  |  |  | -11.3% | 9.57% |  |  |  | -0.0130 | 0.0090 to 0.0200 | -0.1117 to -0.0890
PALOUSE-WOLFCAMP 138KV | 🟡 Watch | 49238.51 | HE18, HE17, HE16 | 30.57% | [12 empty] | -0.0378 to -0.0171 | -0.0004 to 0.0004 | 0.0030 to 0.0050
LPLMK-LPLNE 115KV | 🟡 Watch | 266579.96 | HE21, HE22, HE20 | 1.044% |  |  | 0.574% |  |  | 1.594% | 1.487% | [5 empty] | 0.0146 to 0.0161 | -0.0063 to -0.0048 | -0.0016 to -0.0004
CRDSW-OLNEY 69KV | 🟡 Watch | 14861.86 | HE17, HE18, HE16 | [12 empty] | 78.68% | — | 0.0350 | — | Mineral Wells (North): +0.0350
HONDOCK-DEVINESW 69KV | 🟡 Watch | 57961.31 | HE16, HE18, HE17 |  | -5% |  | -6% | -6.4% | [8 empty] | — | — | —
I_FW_N | 🟡 Watch | 20645.72 | HE5, HE6, HE4 | 9% | [5 empty] | 15.66% | 13.74% |  |  |  | -4% | -6% | 0.1200 to 0.1580 | -0.0480 to -0.0410 | —
CARVER-TINSLEY 138KV | 🟡 Watch | 14200.33 | HE21, HE20, HE22 | -7% | 9% |  | 32.32% | 21% | [8 empty] | -0.0150 | — | 0.0150 to 0.0230
BIG_FOOT-PLEASANT 138KV | 🟡 Watch | 26156.41 | HE16, HE13, HE15 |  | -9.2% | -5.34% | -8.8% | -9.8% | [8 empty] | — | — | -0.0100
MASN-KATEMCY 69KV | 🟡 Watch | 32915.57 | HE19, HE18, HE23 | [5 empty] | 25.1% | [7 empty] | 0.0040 | 0.0005 to 0.0010 | -0.0030 to -0.0020
KLNSW-HHSTH 138KV | 🟡 Watch | 42121 | HE22, HE23, HE2 | -5% | [5 empty] | -4.8% | -4.8% |  |  | -4% |  |  | -0.0480 | -0.0190 to 0.0010 | 0.0188 to 0.0200
SAMSW-VENSW 345KV | 🟡 Watch | 20889.84 | HE11, HE12, HE13 |  | -5.3% | -5.6% |  | -4.4% |  |  |  | -5.6% | -4% |  | 5.3% | 5% | — | 0.0530 to 0.0820 | -0.0570 to -0.0490
MADDUX-TREADWEL 138KV | 🟡 Watch | 18278.19 | HE17, HE18, HE16 | [5 empty] | 39.25% | [7 empty] | -0.0350 | — | —
PRLSW-CONSW 345KV | 🟡 Watch | 8553.5 | HE2, HE4, HE1 | 11.08% |  |  | 4.58% |  |  | 29.04% | 23.37% |  |  | -5.25% | -4.1% | -5% | 0.1350 to 0.2460 | -0.0460 to -0.0410 | -0.0270 to -0.0190
MAXWELL-HAMILTON 138KV | 🟡 Watch | 14519.92 | HE2, HE24, HE1 | -5% | 5% |  | 22.98% | 14.32% | [8 empty] | -0.0130 | — | 0.0120 to 0.0150
LNGSW-CONSW 345KV | 🟡 Watch | 30989.79 | HE1, HE2, HE24 | 8% | [5 empty] | 21.3% | 20% | [5 empty] | 0.0800 to 0.2000 | -0.0220 to -0.0210 | -0.0220 to -0.0200
SONR-ATSO 69KV | 🟡 Watch | 93639.82 | HE1, HE3, HE2 | 5% |  |  | 1.4% | [9 empty] | 0.0026 to 0.0073 | 0.0001 to 0.0002 | 0.0005 to 0.0010
LAKENASW-SAMATHIS 69KV | 🟡 Watch | 79252.55 | HE1, HE4, HE24 | 7.252% | [12 empty] | 0.0020 to 0.0080 | -0.0010 | -0.0008 to -0.0004
BRUNI 138KV | 🟡 Watch | 263224.34 | HE23, HE22, HE21 |  | 1.044% |  |  | 1.044% | [8 empty] | 0.0008 to 0.0009 | 0.0005 to 0.0006 | -0.0264 to 0.0018
CRTRVLLE-HILGR 138KV | 🟡 Watch | 66977.23 | HE1, HE2, HE23 | [6 empty] | 4% | 4% | [5 empty] | 0.0363 to 0.1360 | -0.0069 to -0.0066 | -0.0050 to -0.0040 | Garden City (West): +0.1360
ARGYL-LWSVH 138KV | 🟡 Watch | 359570.46 | HE1, HE2, HE24 | [11 empty] | 1.469% |  | -0.0137 to -0.0121 | -0.0278 to 0.0208 | 0.0003 to 0.0029
NORTMC-CROSSOVE 138KV | 🟡 Watch | 8837.72 | HE19, HE17, HE16 | 34.17% |  |  | 9.187% | 5.7% |  | -2.8% | -2.35% | [5 empty] | -0.0350 to -0.0160 | — | —
LA_PALMA-HAINE_DR 138KV | 🟡 Watch | 157434.95 | HE17, HE16, HE18 |  |  | 1.138% | [5 empty] | 1.856% |  |  |  |  | -0.0026 to -0.0026 | -0.0028 to -0.0027 | -0.0144 to 0.0392 | Falfurrias (Coastal): +0.0392
GN-PZ 138KV | 🟡 Watch | 25619.24 | HE16, HE14, HE17 | [9 empty] | 18.32% |  |  |  | — | — | —
PILONCIL-NLARSW 138KV | 🟡 Watch | 4162.67 | HE16, HE15, HE17 |  | -26.48% | 23.81% | -9.445% | -12.96% |  |  |  | 7.6% |  |  |  |  | — | — | 0.0210 to 0.0500 | Falfurrias (Coastal): +0.0500
MV_BURNS-MV_HBRG4 138KV | 🟡 Watch | 21330.38 | HE17, HE18, HE19 | [8 empty] | 15.34% |  |  |  |  | — | — | -0.0100
CATARINA-ASHERTON 138KV | 🟡 Watch | 3299.99 | HE22, HE21, HE20 |  | -73.2% | -9.013% | 7.22% |  |  |  |  | -5.14% |  |  |  |  | — | — | -0.0510 to -0.0230 | Falfurrias (Coastal): -0.0510
BR-HOC 138KV | 🟡 Watch | 26713.59 | HE16, HE15, HE17 | [9 empty] | 9.515% |  |  |  | -0.0100 | -0.0130 to -0.0110 | -0.0250 to -0.0200
BOW 69KV | 🟡 Watch | 36478.42 | HE9, HE8, HE20 | [12 empty] | -5% | -0.0030 | -0.0020 to 0.0100 | -0.0030 to 0.0001
MCCAMY | 🟡 Watch | 4254.06 | HE13, HE12, HE14 | -24.66% |  |  | -11.28% | -6.874% | [8 empty] | -0.1440 to 0.0366 | 0.0100 to 0.0110 | — | Gomez (West): -0.1440
CMNSW-CMNTP 138KV | 🟡 Watch | 31078.31 | HE17, HE19, HE18 | [10 empty] | 5% |  |  | -0.0150 | 0.0100 to 0.0570 | -0.0060 | Mineral Wells (North): +0.0570
UVALDE-READING 138KV | 🟡 Watch | 3280.03 | HE19, HE18, HE17 |  | -8.093% |  | -20.46% | -8.935% | [8 empty] | — | — | 0.0180
WOLFCAMP-SANTARIT 138KV | 🟡 Watch | 3322.27 | HE17, HE16, HE19 | 31.74% | [12 empty] | -0.0380 to -0.0170 | — | —
LHSES-PRCSW 138KV | 🟡 Watch | 15846.42 | HE20, HE19, HE17 | [11 empty] | -5% |  | — | -0.0500 to -0.0450 | —
LAREDO-DEL_MAR 138KV | 🟡 Watch | 12390.2 | HE23, HE24, HE22 |  |  | 6% | [10 empty] | — | — | —
COLETO CREEK-VICTORIA | 🟡 Watch | 6622.44 | HE20, HE22, HE21 | [8 empty] | -9.17% |  |  |  |  | — | — | -0.1100 to 0.0460
FMRVL-RYSSW 345KV | 🟡 Watch | 4009.58 | HE17, HE16, HE15 | [11 empty] | 5.227% | -3.425% | -0.0200 to -0.0190 | -0.0266 to 0.0585 | — | Lufkin South (North): +0.0585
VEALMOOR-KOCHTAP 138KV | ⚫ Low Priority | 294667.84 | HE23, HE24, HE22 | 2.331% |  |  | 1.012% |  |  | 5.24% | 4.47% | [5 empty] | 0.0424 to 0.0564 | -0.0107 to -0.0099 | -0.0047 to -0.0026
SNDHT-WLFSW 138KV | ⚫ Low Priority | 54270.9 | HE4, HE2, HE1 | [6 empty] | -44.87% | 7% | [5 empty] | -0.0163 to 0.0828 | -0.0064 to -0.0058 | -0.0004
WCRYSTS-CARIZOS 69KV | ⚫ Low Priority | 39682.54 | HE7, HE8, HE5 |  | -5% |  | 12.6% | 19% | [8 empty] | 0.0050 | 0.0004 to 0.0010 | -0.0070 to -0.0030
JEWET-BBSES 345KV | ⚫ Low Priority | 22370.98 | HE21, HE20, HE8 | 4% | -4% | -5% |  |  |  | 4% | 4% | -5% | -10% | 6.8% | 12.87% | 8.33% | 0.0400 | 0.0870 to 0.1200 | -0.0800 to -0.0500
ABNTHWST 138KV | ⚫ Low Priority | 101250.18 | HE17, HE16, HE18 | [10 empty] | 13.95% |  |  | -0.0047 to -0.0041 | -0.0021 to 0.0062 | -0.0026 to -0.0025
KLNSW-STAGE 138KV | ⚫ Low Priority | 80643.09 | HE22, HE23, HE24 | -4% | [5 empty] | -4% | -4% | 2.1% |  | -3% |  |  | -0.0440 to -0.0044 | -0.0210 to -0.0020 | 0.0208 to 0.0210
HAMILTON-MAVERICK 138KV | ⚫ Low Priority | 15943.21 | HE17, HE20, HE21 |  | 7.2% |  | -56% | 19.61% | [8 empty] | -0.0190 to -0.0130 | — | 0.0150 to 0.0180
HCKSW 1KV | ⚫ Low Priority | 69902.77 | HE19, HE21, HE20 | -3.5% | [5 empty] | -4% | -4% |  |  |  |  | -3% | -0.0410 to -0.0310 | 0.0170 to 0.0350 | -0.0050 to -0.0007
PILONCIL-CATARINA 138KV | ⚫ Low Priority | 22056.9 | HE22, HE20, HE21 |  | 33.7% | -9.8% | [10 empty] | 0.0100 | — | —
W_BATESV-UVALDE 138KV | ⚫ Low Priority | 12090.77 | HE22, HE4, HE21 |  | -14.97% | -6% | 27.53% | 29.99% | [8 empty] | 0.0100 | — | -0.0250 to -0.0170
VALEXP | ⚫ Low Priority | 8226.78 | HE4, HE3, HE5 | [8 empty] | -98.24% |  |  |  |  | 0.0170 | 0.0170 | 0.0170
MDO-PHR 345KV | ⚫ Low Priority | 18172.47 | HE16, HE14, HE15 |  | -9.1% | -9.6% | -6% | -7.7% |  |  |  | -10% |  |  |  |  | -0.0200 to -0.0190 | — | -0.0920 to -0.0680
FTSSW-VENSW 345KV | ⚫ Low Priority | 24101.09 | HE16, HE15, HE17 |  | -5.69% | -6% | -3.7% | -4.7% | -4.1% |  |  | -6% |  |  |  |  | — | 0.0680 to 0.0930 | -0.0610 to -0.0430
NVKSW-ANARN 69KV | ⚫ Low Priority | 13573.27 | HE18, HE17, HE16 | [12 empty] | 47.6% | — | — | —
OZONA-MIDW 69KV | ⚫ Low Priority | 89022.35 | HE16, HE15, HE13 | 6% | [12 empty] | -0.0016 to -0.0007 | — | -0.0003 to -0.0001
TMPSW-TMPCR 345KV | ⚫ Low Priority | 6604.19 | HE21, HE20, HE4 |  | -9.32% | -9.97% | -5% | -7.37% | -6.1% |  |  | -9.91% | -4.5% | 7.1% | 8.2% | 8.1% | 0.0200 to 0.0320 | 0.0820 to 0.1000 | -0.1000 to -0.0770
ZEN-THW 345KV | ⚫ Low Priority | 10819.9 | HE15, HE14, HE16 | -7.2% |  |  |  |  | -5.3% | -7.7% | -7.5% |  | 12.78% | -84% | -10% | -8% | -0.0480 to -0.0420 | -0.0620 to -0.0570 | 0.0210
DOW-OAS 345KV | ⚫ Low Priority | 8240.51 | HE14, HE16, HE15 |  | -7.22% | -7.68% | -4.8% | -5.99% | -3.4% |  |  | -8.23% | 17.58% |  |  |  | -0.0140 to -0.0110 | 0.0100 to 0.0300 | -0.1300 to -0.0750
MAVERICK-HAMILTON 138KV | ⚫ Low Priority | 5230.46 | HE2, HE4, HE3 | 5.256% | -8.936% |  | 40.61% | -25.82% | [8 empty] | 0.0170 | — | -0.0175 to -0.0138
SNDSW-AUSTRO 345KV | ⚫ Low Priority | 3314.01 | HE16, HE17, HE15 | -6.348% | 14.06% | 15.04% | 8.8% | 11.44% |  | -7.518% | -7.016% | 14.76% |  | -9.626% | -9.504% | -9.9% | -0.0780 to -0.0700 | -0.1000 to -0.0950 | 0.1000 to 0.1538
GANSO-MAVERICK 138KV | ⚫ Low Priority | 6314.84 | HE4, HE6, HE5 |  | -9.232% | -4.424% | 40.19% | [9 empty] | 0.0200 to 0.0300 | — | -0.0230 to -0.0190
RIOHONDO-MV_BURNS 138KV | ⚫ Low Priority | 16376.64 | HE18, HE17, HE19 | [8 empty] | 19.76% |  |  |  |  | — | — | 0.0470 | Falfurrias (Coastal): +0.0470
MADDUX-SAPOWER 138KV | ⚫ Low Priority | 4392.44 | HE7, HE8, HE6 | -6.95% |  |  | -11.67% | -7.369% | -33.6% | [7 empty] | — | — | -0.0100
MILLER-HENLY 138KV | ⚫ Low Priority | 23333.33 | HE17, HE18, HE19 | [5 empty] | -11% | [7 empty] | -0.0100 | — | —
ODESA-ODNTH 138KV | ⚫ Low Priority | 32001.33 | HE23, HE5, HE22 | [7 empty] | 8% | [5 empty] | -0.0280 to 0.1000 | -0.0100 to -0.0080 | -0.0050 to -0.0040
CPSES-MBDSW 345KV | ⚫ Low Priority | 11040.17 | HE20, HE1, HE7 | -6% |  |  |  |  | -4.5% | -5.9% | -5.8% | [5 empty] | -0.0580 to -0.0570 | 0.0260 to 0.0340 | —
SMITHERS-BI 345KV | ⚫ Low Priority | 5229.02 | HE19, HE18, HE17 |  | -3.961% | -4.352% |  | -32.6% |  |  |  | -4.9% |  |  |  |  | — | 0.0100 | -0.0580 to -0.0400
KENDAL-BERGHE 345KV | ⚫ Low Priority | 2556.79 | HE14, HE13, HE12 | -13.83% | 7.977% | 9.654% |  |  | -15.72% | -13.17% | -14.46% | 10.35% |  |  |  |  | -0.1300 to -0.1200 | -0.0340 to -0.0130 | 0.0540 to 0.0760
DOWNIES-MOORE 138KV | ⚫ Low Priority | 5209.02 | HE14, HE16, HE15 |  | -6% |  | -15.52% | -18.2% | [8 empty] | — | — | —
TNFXTAIL-FLAT_TOP 138KV | ⚫ Low Priority | 6210.06 | HE17, HE16, HE15 | [6 empty] | 1.6% | 31.33% | [5 empty] | -0.1000 to 0.2010 | — | —
EXCSW-RNKSW 345KV | ⚫ Low Priority | 3663.34 | HE20, HE21, HE19 | -5.82% |  |  | -3.9% | -3.2% | -4.29% | -6.4% | -6.2% |  |  | -6.6% | 4.448% | -6.8% | -0.0660 to -0.0610 | 0.0390 to 0.1120 | -0.0220 to -0.0120 | Farmersville (North): +0.1120
SAMSW-FVLSW 345KV | ⚫ Low Priority | 4333.4 | HE12, HE11, HE10 |  | -5.577% | -5.843% | -4% | -4.823% |  |  |  | -5.925% |  | 3.57% | 4.524% | 5.485% | 0.0130 | 0.0450 to 0.0770 | -0.0590 to -0.0490
TNP_ONE-TOKSW 345KV | ⚫ Low Priority | 3348.1 | HE15, HE14, HE13 |  | -6.355% | -6.213% | -5.766% | -6.14% | -7.546% |  |  | -5.42% | 6.594% |  | 6.361% |  | -0.0390 to -0.0330 | 0.0330 to 0.0630 | -0.0680 to -0.0470
GT-BG 138KV | ⚫ Low Priority | 11356.14 | HE17, HE16, HE12 | [9 empty] | 14.26% |  |  |  | -0.0100 | -0.0100 | -0.0100
I_KALO | ⚫ Low Priority | 4724.22 | HE13, HE15, HE14 |  |  | 6.5% | [5 empty] | 25.69% |  |  |  |  | -0.0240 | -0.0230 | 0.1990 to 0.3320
BLESSING 345KV | ⚫ Low Priority | 14518.22 | HE22, HE9, HE7 |  |  | 4.1% | [5 empty] | 6.3% |  |  |  |  | — | -0.0120 to -0.0100 | 0.0230 to 0.4790 | Pavlov (Coastal): +0.4790
SANA 138KV | ⚫ Low Priority | 35242.22 | HE6, HE5, HE4 | [10 empty] | 4% |  |  | 0.0040 | -0.0010 to -0.0005 | -0.0090
ELGISW-BUTLER 138KV | ⚫ Low Priority | 5037.87 | HE18, HE16, HE17 | -2% | 4.196% | 4.516% |  |  |  | -2% | -2% | 4.6% |  | -2.7% | -2.6% | -2.7% | -0.0200 | -0.0290 to -0.0260 | 0.0280 to 0.0450
ESTLD-MRVLY 69KV | ⚫ Low Priority | 12489.03 | HE13, HE8, HE9 | [10 empty] | -4.5% |  | 5.3% | — | 0.0130 | —
HOLMAN-CISTERN 345KV | ⚫ Low Priority | 3353.69 | HE21, HE22, HE4 |  | 5.598% | 5.233% | 5.428% | 5.63% | 6.49% |  |  |  | -7.052% |  |  |  | 0.0290 to 0.0380 | 0.0110 | -0.0740 to 0.0530
YELWJCKT-HEXT 69KV | ⚫ Low Priority | 18859.01 | HE14, HE17, HE12 | [5 empty] | 5.9% | [7 empty] | — | — | —
CRD 345KV | ⚫ Low Priority | 16830.01 | HE22, HE2, HE1 | [10 empty] | 6% |  |  | — | 0.1360 | — | Mineral Wells (North): +0.1360
BRACKETT-ESCONDID 138KV | ⚫ Low Priority | 1988.62 | HE18, HE17, HE16 | -4.194% | 10.13% | 4.094% | -32.3% | [9 empty] | -0.0140 | — | 0.0130 to 0.0170
BANDER-MASOCR 138KV | ⚫ Low Priority | 7382.61 | HE16, HE19, HE18 | [5 empty] | -8% | [7 empty] | -0.0260 to -0.0190 | -0.0100 | 0.0100 to 0.0230
CNRSW 345KV | ⚫ Low Priority | 3048 | HE15, HE14, HE16 | [11 empty] | -14.08% |  | — | -0.1400 to -0.1100 | —
EINSTEIN-CRTRVLLE 138KV | ⚫ Low Priority | 4113.48 | HE8, HE7, HE9 | [6 empty] | 4.849% | 3.842% | [5 empty] | 0.0350 to 0.1350 | — | — | Garden City (West): +0.1350
🆕 NEW — Identified via updated site-level crosswalk (not yet priority-classified)
PEARSALL-POTEETS 69KV | 🆕 New | 167352.76 | HE17, HE18, HE16 |  | -0.01753 | -0.01336 |  | -0.01269 | [8 empty] | — | — | — | Poteet (Coastal): +0.3910
BCPSW-AZLES 138KV | 🆕 New | 7518.99 | HE18, HE19, HE17 | [10 empty] | 0.03 |  | 0.04 | — | 0.2250 | — | Mineral Wells (North): +0.2250
Columns R–U (added): West TX (10 sites), North TX (4 sites), and Coastal (5 sites) ranges show the min-to-max shift factor across that region's non-premium-tier sites for this line — use as a rough regional exposure gauge, not a per-site number. "—" = no meaningful exposure in that region. Notable Non-Premium Site(s) calls out any single site whose exposure is well above its regional peers (worth tracking individually rather than folding into the range).

## ⏰ Hour Guide
HOURLY DISCHARGE GUIDE — Historical Shadow Pricing by Hour Ending (Apr 2025 – May 2026)
Values = Total $ shadow pricing accumulated in that hour over the study period. Higher = more congestion exposure in that hour. Color intensity = relative magnitude.
Line / Constraint | Priority | Total $ | HE1 | HE2 | HE3 | HE4 | HE5 | HE6 | HE7 | HE8 | HE9 | HE10 | HE11 | HE12 | HE13 | HE14 | HE15 | HE16 | HE17 | HE18 | HE19 | HE20 | HE21 | HE22 | HE23 | HE24
TWINBU-HARGROVE 138KV | 🟢 Active | 812338.3 | 67031.56 | 78042.27 | 85676.48 | 93412.97 | 101422.32 | 95386.19 | 78245.67 | 52048.79 | 13496.03 | 9337.29 | 5147.96 | 1781.44 | 1755.51 | 2254.73 | 1723.31 | 1844.91 | 880.08 | 977.51 | 4184.01 | 6324.09 | 12226.18 | 18850.77 | 28465.14 | 51823.09
LARDVNTH-LASCRUCE 138KV | 🟢 Active | 150133.74 | 5292.9 | 4016.18 | 2584.08 | 1441.52 | 1460.88 | 1506.22 | 1972.63 | 1300.26 | 1077.74 | 1765.52 | 2139.03 | 2022.88 | 1587.54 | 1384.82 | 1552.48 | 2858.78 | 4289.72 | 7677.17 | 15748.88 | 27679.73 | 27663.42 | 18016.5 | 9419.33 | 5675.53
FORTMA-YELWJCKT 138KV | 🟢 Active | 103773.93 | 6927.47 | 7504.88 | 5776.69 | 7337.18 | 6465.42 | 4479.64 | 4070.58 | 3102.16 | 982.11 | 163.73 | [5 empty] | 6 | 697.78 | 6238.74 | 7077.57 | 8859.78 | 9917.69 | 8495.72 | 8672.96 | 6997.83
STP-ELMCREEK 345KV | 🟢 Active | 89021.72 | 3789.99 | 3172.48 | 3064.52 | 3075.23 | 3171.1 | 4517.58 | 5196.07 | 5373.49 | 1727.02 | 557.12 | 454.9 | 439.05 | 423.35 | 429.37 | 190.28 | 55.57 | 707.6 | 3364.43 | 7098.8 | 5392.5 | 9584.25 | 11626.19 | 9016.85 | 6593.98
TREADWEL-YELWJCKT 138KV | 🟢 Active | 99801.11 | 2040.61 | 1496.75 | 1311.53 | 1197.23 | 802.83 | 897.6 | 1087.27 | 822.49 | 1233.12 | 2381.19 | 4127.3 | 5372.08 | 5905.86 | 7345.69 | 8718.37 | 9151 | 10821.32 | 10302.42 | 9283.54 | 6435.89 | 2234.67 | 2028.78 | 2482.7 | 2320.87
LASCRUCE-MILO 138KV | 🟢 Active | 59751.88 | 2698.34 | 2135.24 | 2595.03 | 2635.43 | 2780 | 2630.49 | 2489.77 | 2672.6 | 1383.99 | 642.14 | 909.49 | 921.82 | 696.89 | 570.21 | 712.37 | 1204.27 | 2156.75 | 3398.77 | 5910.35 | 6139.76 | 4375.1 | 4356.49 | 2805.09 | 2931.49
WESTEX | 🟢 Active | 8701.73 | 305.77 | 249.86 | 192.79 | 152.03 | 148.14 | 170.43 | 204.97 | 284.51 | 250.59 | 377.52 | 516.63 | 532.59 | 469.9 | 437.06 | 463.27 | 492.54 | 504.42 | 463.31 | 543.96 | 550.41 | 345.63 | 311.2 | 362.19 | 372.01
LNGSW-PRLSW 345KV | 🟢 Active | 56393.44 | 4609.85 | 4522.05 | 4308.79 | 3904.78 | 3499.42 | 3088.33 | 2084.55 | 1380.77 | 580.35 | 446.24 | 699.9 | 787.08 | 835.66 | 827.62 | 821.14 | 1045.78 | 1090.38 | 1627.47 | 1704.78 | 2261.65 | 3222.73 | 4110.84 | 4426.32 | 4506.96
E_PASP | 🟢 Active | 84322.9 | 1311.99 | 791.19 | 474.4 | 433.31 | 368.34 | 622.26 | 345.87 | 317.93 | 262.53 | 1179.02 | 1305.35 | 1513.93 | 1433.25 | 1890.45 | 3115.82 | 4385.6 | 5650.32 | 8258.88 | 13547.46 | 17042.59 | 8067.77 | 7311.33 | 2719.71 | 1973.6
NLARSW-PILONCIL 138KV | 🟢 Active | 59654.53 | 5617.55 | 5546.82 | 4468.11 | 3991.56 | 3535.61 | 4411.91 | 1968.52 | 1849.97 | 1163.11 | 779.73 | 536.63 | 449.55 | 548.07 | 520.62 | 541.11 | 717.18 | 1103.9 | 1406.76 | 1016.29 | 2775.17 | 2575.22 | 2936.22 | 4839.01 | 6355.91
MGSES-CATSW 345KV | 🟢 Active | 31442.57 | 1614.56 | 1865.31 | 1860.67 | 1941.16 | 1443.57 | 1847.13 | 1313.93 | 1093.3 | 742.74 | 241.84 | 424.34 | 308.61 | 171.39 | 27.01 | 53.78 | 167.27 | 797.88 | 1641.74 | 2939.11 | 2708.21 | 1879.05 | 1197.21 | 3335.75 | 1827.01
LOBO-LARDVNTH 138KV | 🟢 Active | 37951.02 | 1612.49 | 1294.51 | 880.24 | 569.87 | 429.57 | 453.71 | 562.4 | 596.74 | 584.41 | 659.64 | 921.51 | 759.11 | 742.65 | 932.14 | 1077.88 | 1433.85 | 2046.02 | 3113.17 | 3340.8 | 3034.76 | 3335.27 | 4415.43 | 2989.97 | 2164.88
ESCONDID-GANSO 138KV | 🟢 Active | 33325.75 | 2272.75 | 1823.59 | 1882.15 | 1906 | 1986.73 | 1528.84 | 1608.22 | 2658.7 | 2300.74 | 1011.41 | 656.93 | 1085.99 | 735.09 | 644.99 | 605.74 | 479.31 | 1386.94 | 1190.33 | 825.08 | 858.59 | 1303.51 | 1002.98 | 1527.27 | 2043.87
BCESW-SNDSW 345KV | 🟢 Active | 32240.3 | 288.26 | 253.67 | 253.78 | 156.02 | 59.26 | 75.07 | 205.46 | 296.05 | 629.96 | 1399.44 | 1396.89 | 1976.95 | 2257.87 | 2949.19 | 3758.9 | 4072.73 | 4766.5 | 4503.34 | 1598.82 | 233.58 | 279.89 | 235.08 | 272.5 | 321.09
LNGSW-CONSW 345KV | 🟢 Active | 30989.79 | 4086.86 | 3745.26 | 3211.53 | 2996.59 | 2905.08 | 2210.82 | 1592.44 | 672.79 | 254.66 | 266.87 | 174.72 | 177.29 | 145.49 | 141.08 | 122.16 | 83.53 | 83.41 | 113.11 | 546.52 | 356.42 | 556.64 | 1059.67 | 2265.1 | 3221.75
YELWJCKT-FORTMA 138KV | 🟢 Active | 18780.08 | 838.61 | 708.63 | 866.54 | 1018.41 | 1120.39 | 1514.25 | 1695.8 | 998.7 | 986.58 | 974.57 | 418.53 | 462.55 | 425.85 | 511.04 | 689.88 | 584.12 | 1013.98 | 419.11 | 329.65 | 344.62 | 809.24 | 772.81 | 675.08 | 601.14
Legend: | 🟢 Active = detailed MCC analysis completed | 0
ASHERTON-CATARINA 138KV | 🟡 Watch | 23033.53 | [8 empty] | 333.66 | 1115.4 | 2020.27 | 2963.52 | 3376.63 | 2919.27 | 2602.16 | 2808.89 | 2593.83 | 1548.22 | 693.24 | 58.44
MRVLY-ESTLD 69KV | 🟡 Watch | 134306.39 | 2632.71 | 3167.6 | 3044.79 | 3037.09 | 3602.14 | 6913.3 | 8532.41 | 9743.95 | 5032.52 | 1708.56 | 673.82 | 434.39 | 522.02 | 268.07 | 2631.71 | 2097.29 | 3176.64 | 7733.18 | 14859.49 | 15436.69 | 12993.3 | 11194.25 | 8358.29 | 6512.18
STP-WAP 345KV | 🟡 Watch | 33834.4 | 1.02 | [7 empty] | 93.47 | 583.51 | 1310.42 | 2267.37 | 4378.74 | 4131.06 | 4376.04 | 5652.8 | 6104.37 | 4051.3 | 867.58 | 16.72
PALOUSE-WOLFCAMP 138KV | 🟡 Watch | 49238.51 | [6 empty] | 105.29 | 407.76 | 596.71 | 1520.39 | 2233.12 | 3432.43 | 4606.39 | 5094.25 | 5834.43 | 5859.12 | 6010.54 | 6255.62 | 4731.67 | 2377.63 | 173.16
LPLMK-LPLNE 115KV | 🟡 Watch | 266579.96 | 9373.8 | 9871.73 | 9413.47 | 11832.5 | 12975.74 | 12869.99 | 13338.17 | 11749.25 | 5067.11 | 3738.85 | 3417.93 | 3017.02 | 3405.03 | 3827.47 | 4683.52 | 5228.69 | 6950.44 | 10822.07 | 22395.26 | 23860.37 | 26134.15 | 25904.33 | 16141.9 | 10561.17
CRDSW-OLNEY 69KV | 🟡 Watch | 14861.86 | 4.5 | 1.31 | 1.9 |  | 405.43 | 13.12 |  |  |  | 18.68 | 72.17 | 128.38 | 434.43 | 1025.09 | 1775.1 | 2729.23 | 3263.9 | 3193.1 | 1504.84 | 274.5 | 10.53 |  | 4.04 | 1.61
HONDOCK-DEVINESW 69KV | 🟡 Watch | 57961.31 | [7 empty] | 19.02 | 243.15 | 1567.33 | 2907.55 | 3372.99 | 5123.2 | 6627.85 | 7603.35 | 8854.54 | 7704.46 | 8180.35 | 5757.52
I_FW_N | 🟡 Watch | 20645.72 | 1099.23 | 1401.06 | 1751.5 | 1826.9 | 2151.59 | 1942.22 | 1414.12 | 1533.12 | 854.4 | 112.26 | 84.83 | 55.38 | 57.12 | 53.85 | 92.8 | 41.21 | 131.4 | 82.22 | 151.14 | 465.94 | 997.42 | 1365.76 | 1634.32 | 1345.93
CARVER-TINSLEY 138KV | 🟡 Watch | 14200.33 | 625.15 | 553.62 | 320.19 | 364.32 | 582.27 | 201.81 | 66.6 | 75 | 165.94 | 672.82 | 846.51 | 593.15 | 501.89 | 220.39 | 231.33 | 799.32 | 766.59 | 771.24 | 366.03 | 1396.82 | 1474.42 | 996.72 | 888.65 | 719.55
BIG_FOOT-PLEASANT 138KV | 🟡 Watch | 26156.41 | [8 empty] | 51.2 | 888.78 | 1963.97 | 3301.9 | 3954.66 | 3422.34 | 3690.71 | 3977.51 | 3264.92 | 1465.73 | 173.85 | 0.84
MASN-KATEMCY 69KV | 🟡 Watch | 32915.57 | 462.62 | 1.95 | 37.28 | 31.56 | 429.36 | 146.9 | 338.39 | 3483.54 | 2612.74 | 1263.97 | 760.92 | [6 empty] | 4537.22 | 4802.99 | 2138.24 | 2877.97 | 3484.48 | 3507.62 | 1997.82
KLNSW-HHSTH 138KV | 🟡 Watch | 42121 | 2347.35 | 2481.2 | 2411.82 | 2213.21 | 1980.95 | 1981.37 | 1947.01 | 2348.68 | 1511.67 | 1248.43 | 914.67 | 717.31 | 672.93 | 710.72 | 569.06 | 446.46 | 759.77 | 1327.29 | 2327.88 | 2284.31 | 2469.9 | 3094.09 | 2879.17 | 2475.75
SAMSW-VENSW 345KV | 🟡 Watch | 20889.84 | [8 empty] | 317.47 | 2511.18 | 3425.87 | 3383.89 | 3195.6 | 2827.63 | 2197.21 | 1730.95 | 785.61 | 394.73 | 119.7
MADDUX-TREADWEL 138KV | 🟡 Watch | 18278.19 | 184.3 | 145.59 | 123.73 | 127 | 33.79 | 73.4 | 147.31 | 100.89 | 17.41 | 171.62 | 276.95 | 617.72 | 1018.32 | 1359.94 | 1815.76 | 2318.53 | 3327.37 | 2557.19 | 1668.52 | 1087.54 | 314.6 | 320.98 | 258.74 | 210.99
PRLSW-CONSW 345KV | 🟡 Watch | 8553.5 | 690.68 | 913.32 | 566.36 | 692.95 | 655.64 | 433.52 | 312.18 | 185.38 | 138.07 | 180.76 | 218.65 | 141.86 | 50.81 | 46.44 | 65.94 | 55.31 | 4.46 | 318.76 | 393.73 | 267.11 | 481.63 | 609.67 | 513.09 | 617.18
MAXWELL-HAMILTON 138KV | 🟡 Watch | 14519.92 | 1371.62 | 1628.62 | 1351.71 | 1066.23 | 925.01 | 592 | 680.58 | 541.95 | 414.63 | 170.11 | 141.42 | 54.33 | 13.92 | 29.66 | 28.3 | 53.84 | 74.95 | 190.22 | 636.63 | 646.34 | 541.79 | 708.72 | 1178.57 | 1478.77
LNGSW-CONSW 345KV | 🟡 Watch | 30989.79 | 4086.86 | 3745.26 | 3211.53 | 2996.59 | 2905.08 | 2210.82 | 1592.44 | 672.79 | 254.66 | 266.87 | 174.72 | 177.29 | 145.49 | 141.08 | 122.16 | 83.53 | 83.41 | 113.11 | 546.52 | 356.42 | 556.64 | 1059.67 | 2265.1 | 3221.75
SONR-ATSO 69KV | 🟡 Watch | 93639.82 | 8003.2 | 7850.59 | 7882.16 | 7830.67 | 7086.51 | 7565.07 | 5873.66 | 5270.89 | 3777.6 | 3998.96 | 1519.44 | 620.13 | 308.09 | 216.82 | 235.11 | 297.52 | 162.86 | 289.44 | 744.93 | 1399.59 | 2948.97 | 4632.99 | 7845.21 | 7279.41
LAKENASW-SAMATHIS 69KV | 🟡 Watch | 79252.55 | 11497.71 | 8541.15 | 6992.86 | 9570.23 | 7538.91 | 6370.11 | 2965.11 |  |  | 16.54 | 107.66 | 2073.32 | 1309.31 | 36.12 | 47.38 | 12.75 | 27.2 |  |  | 445.87 | 2970.27 | 5165.65 | 4968.28 | 8596.12
BRUNI 138KV | 🟡 Watch | 263224.34 | 15349.56 | 13677.75 | 10694.08 | 13676.63 | 17442.36 | 15548.45 | 13837.84 | 11473.16 | 7595.51 | 5881.32 | 2295.36 | 3318.81 | 4311.3 | 5461.83 | 5240.61 | 6049.19 | 4767.39 | 8401.55 | 10321.95 | 13538.32 | 17831.16 | 19291.42 | 20074.73 | 17144.06
CRTRVLLE-HILGR 138KV | 🟡 Watch | 66977.23 | 7020.09 | 6266.66 | 4919.49 | 4259.09 | 3567.73 | 3435.13 | 2862.97 | 2765.02 | 1893.86 | 249.79 | 689.63 | 517.19 | 412.86 | 85.78 | 751.13 | 949.08 | 1299.32 | 1445.65 | 2069.65 | 2776.36 | 3403.54 | 5138.64 | 5349.11 | 4849.46
ARGYL-LWSVH 138KV | 🟡 Watch | 359570.46 | 20965.26 | 20380.65 | 18615.21 | 16982.49 | 15813.17 | 15767.84 | 16972.88 | 15773.53 | 12737.93 | 12954.04 | 12379.96 | 12122.29 | 13231.87 | 13414.94 | 13763.08 | 14572.82 | 14653.54 | 9268.01 | 9098.79 | 11572.38 | 15032.34 | 16675.01 | 17520.77 | 19301.66
NORTMC-CROSSOVE 138KV | 🟡 Watch | 8837.72 | [9 empty] | 39.81 | 10.61 | 193.52 | 476.05 | 815.3 | 1194.7 | 1489.93 | 1546.13 | 1376.95 | 1583.76 | 110.96
LA_PALMA-HAINE_DR 138KV | 🟡 Watch | 157434.95 | 2007.36 | 1498.5 | 955.3 | 1179.14 | 649.95 | 662.18 | 1138.03 | 1170.9 | 2606.9 | 4689.33 | 5893.81 | 8060.67 | 10321.91 | 12148.7 | 14938.22 | 18273.92 | 19748.9 | 17889.71 | 11539.64 | 7304.47 | 5321.6 | 4421.88 | 2913.09 | 2100.84
GN-PZ 138KV | 🟡 Watch | 25619.24 | 66.68 | 32.62 | 2.43 | 0.55 |  |  | 1.8 | 0.86 | 76.94 | 560.75 | 1094.6 | 1812.68 | 3093.01 | 3365.08 | 3201.45 | 5203.15 | 3306.83 | 2493.54 | 715.96 | 146.14 | 128.89 | 91.6 | 86.7 | 136.98
PILONCIL-NLARSW 138KV | 🟡 Watch | 4162.67 | [8 empty] | 0.69 | 60.43 | 113.4 | 168.03 | 407.59 | 560.35 | 844.98 | 1077.23 | 725.64 | 139.68 | 64.65
MV_BURNS-MV_HBRG4 138KV | 🟡 Watch | 21330.38 | 113.87 | 3.77 | 146.43 | 37.55 | [5 empty] | 16.29 | 393.46 | 739.86 | 957.48 | 1274.3 | 1942.22 | 2435.39 | 3596.77 | 3322.57 | 3266.36 | 1218.55 | 631.1 | 475.07 | 449.24 | 310.1
CATARINA-ASHERTON 138KV | 🟡 Watch | 3299.99 |  |  |  | 41.98 | 4.61 | 96.84 | 153.55 | 63.81 | 21.04 | 7.66 | 2.94 |  | 0.91 |  |  | 0.41 | 8.78 | 24.91 | 98.97 | 493.6 | 694.58 | 1115.83 | 347.8 | 121.77
BR-HOC 138KV | 🟡 Watch | 26713.59 | 332.51 | 287.6 | 388.6 | 344.67 | 272.92 | 147.08 | 280.18 | 389.13 | 517.26 | 811.18 | 1288.83 | 1718.61 | 2129.86 | 2934.82 | 3452.33 | 3887.98 | 3134.25 | 1445.88 | 674.33 | 561.59 | 412.34 | 488.24 | 467.28 | 346.12
BOW 69KV | 🟡 Watch | 36478.42 | 140.02 | 254.81 | 437.9 | 820.02 | 178.09 | 576.98 | 3076.23 | 3287.75 | 4134.9 | 2544.02 | 2006.54 | 1191.38 | 1264.17 | 1202.82 | 1195.11 | 728.08 | 652.74 | 1261.83 | 1913.47 | 3155.84 | 2162.21 | 2386.13 | 1250.84 | 656.54
MCCAMY | 🟡 Watch | 4254.06 | 39.52 | 10.71 | [5 empty] | 0.33 | 29.37 | 307.44 | 451.21 | 591.56 | 605.54 | 494.43 | 422.65 | 405.86 | 360.84 | 325.9 | 113.65 | 8.09 | 54.01 | 5.26 | 18.38 | 9.31
CMNSW-CMNTP 138KV | 🟡 Watch | 31078.31 | 732.67 | 828.35 | 678.43 | 559.72 | 529.04 | 659.52 | 459.88 | 750.46 | 551.55 | 774.35 | 980.56 | 1226.23 | 1632.21 | 1603.99 | 2091.09 | 2240.06 | 3034.23 | 2647.55 | 2695.64 | 2096.69 | 1339.35 | 1140.51 | 1128.46 | 697.77
UVALDE-READING 138KV | 🟡 Watch | 3280.03 | [8 empty] | 16.1 | 55.67 | 44.05 | 51.89 | 75.01 | 152.11 | 145.23 | 232.22 | 385.95 | 891.77 | 1018.7 | 211.33
WOLFCAMP-SANTARIT 138KV | 🟡 Watch | 3322.27 | [9 empty] | 13.43 |  |  |  |  | 307.36 | 785.01 | 824.12 | 292.82 | 426.13 | 274.18 | 194.6 | 191.85 | 12.77
LHSES-PRCSW 138KV | 🟡 Watch | 15846.42 | 15.99 | [5 empty] | 69.68 | 95.54 |  |  |  | 8.66 | 497.14 | 797.25 | 1456.82 | 1082.69 | 1979.92 | 1617.6 | 2933.45 | 3053.98 | 1349.65 | 718.27 | 155.53 | 14.25
LAREDO-DEL_MAR 138KV | 🟡 Watch | 12390.2 | 1631.85 | 594.25 | 240.53 | 10.03 |  | 48.1 | 16.4 |  | 61.85 | 379.63 | 409.9 | 240.13 | 159.39 | [8 empty] | 2034.64 | 3808.83 | 2754.67
COLETO CREEK-VICTORIA | 🟡 Watch | 6622.44 | 328.54 | 399.76 | 211.03 | 237.85 | 108.36 | 10.8 | 18.63 | 0.33 | 1.57 | 59.39 | 134.48 | 102.48 | 161.4 | 216.4 | 206.62 | 472.99 | 429.71 | 357.27 | 513.7 | 797.81 | 533.2 | 555.47 | 499.84 | 264.81
FMRVL-RYSSW 345KV | 🟡 Watch | 4009.58 | [9 empty] | 10.31 | 81.76 | 186.48 | 456.45 | 565.3 | 633.55 | 891.03 | 1009.58 | 152.34 | 22.78
HEAT MAP LEGEND: | [10 empty] | >70% of peak | 40-70% | 15-40% | 5-15% | <5%